## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 4101 | 3200 | 3239 | 800 | 862 | 20% | 21.02%
RTU-2 | KITCHEN | 4000 | 3729 | 3200 | 2914 | 800 | 815 | 20% | 21.86%
RTU-3 | KITCHEN | 4000 | 3676 | 3200 | 2813 | 800 | 863 | 20% | 23.48%
RTU-4 | DINING AREA | 2000 | 1949 | 1600 | 1511 | 400 | 438 | 20% | 22.47%
RTU-5 | DINING AREA | 2000 | 1980 | 1600 | 1544 | 400 | 436 | 20% | 22.02%
RTU-6 | DINING AREA | 3150 | 3027 | 2520 | 2340 | 630 | 687 | 20% | 22.7%
RTU-7 | DINING AREA | 3150 | 3014 | 2520 | 2354 | 630 | 660 | 20% | 21.9%
RTU-8 | DINING AREA | 2100 | 2232 | 1680 | 1956 | 420 | 276 | 20% | 12.37%
RTU-9 | DINING AREA | 3150 | 3248 | 3150 | 3248 | 0 | 0 | 0% | 0%
RTU-10 | DINING AREA | 2100 | 1705 | 1680 | 1364 | 420 | 341 | 20% | 20%
RTU-11 | DINING AREA | 2100 | 1335 | 1680 | 1047 | 420 | 288 | 20% | 21.57%
RTU-12 | DINING AREA | 1260 | 1284 | 1260 | 1284 | 0 | 0 | 0% | 0%
MUA-1 | KITCHEN | [8 empty] | 2505 | 2552
MUA-2 | KITCHEN | [8 empty] | 2630 | 2669
MUA-3 | KITCHEN | [8 empty] | 1210 | 1164
KEF-1 | HOOD #2 + #3 | [10 empty] | 4339 | 4411
KEF-2 | NO LONGER EXISTS | [10 empty] | 0 | 0
KEF-3 | HOOD #6 | [10 empty] | 1500 | 1456
KEF-4 | OVEN | [10 empty] | 1050 | 1081
KEF-5 | DISHWASHER | [10 empty] | 1488 | 1526
KEF-6 | HOOD #4 | [10 empty] | 1706 | 1732
KEF-7 | HOOD #5 | [10 empty] | 1706 | 1674
EF-1 | RESTROOM | [12 empty] | 75 | 81
EFA-1 | RESTROOM | [12 empty] | 75 | 68
EF-2 | RESTROOM | [12 empty] | 75 | 65
EFA-2 | RESTROOM | [12 empty] | 75 | 115
TOTALS |  | 33010 | 31280 | 27290 | 25614 | 5720 | 5666 |  |  | 6345 | 6385 | 11789 | 11880 | 300 | 329
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 12065 | 12051 |  | FRONT |  | [3] | [8 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 12089 | 12209 |  | SIDE |  | [3] |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | -24 | -158 |  | REAR |  | [3] | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
882 OA MISSING FROM RTU-9 AND RTU-12
88 CFM DIVIDED EVENLY BETWEEN REMAINING 10 RTUS
NOTES:
[1] KEF-2 NO LONGER EXISTS. [2] Due to RTU-9 and RTU-12 not having outside aire intakes, and RTU-8, 10 and 11 having very small outside air intakes causing low outside airflow, actual net buidling airflow is negative. [3] Due to a refridgerent leak, RTU-1 was shut down at the time of final testing. Unable to obtain accurate building pressure.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0