SUMMARY

Included in this TAB report for Lovesac is TAB data for one rooftop unit, and one restroom ceiling fan. Rooftop units were balanced to within +/-10% by reading air devices and adjusting fan speed via motor pulley adjustment. It will be noted that the terminal devices added to 2800 cfm and were each proportionally raised to obtain 3000cfm total, per unit design. Air devices were then balanced to within +/- 10% unless noted. Due to shipping delays the economizer for the RTU has not arrived and minimum Outdoor air could not be set. NTAB will return to set minimum Outdoor air once the economizer is installed. Restroom ceiling exhaust fans were read with a flow hood and confirmed to be within +/-10% of design flow.