## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3581 | 2900 | 3064 | 500 | 517 | 14.71% | 14.44%
RTU-2 | DINING | 4000 | 3985 | 3000 | 2965 | 1000 | 1020 | 25% | 25.6%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1871
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3272
EF-2 | RESTROOM | [12 empty] | 150 | 160
TOTALS |  | 7400 | 7566 | 5900 | 6029 | 1500 | 1537 |  |  | 1950 | 1871 | 3200 | 3272 | 150 | 160
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3450 | 3408 |  | FRONT |  | -0.0022 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3350 | 3432 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | -24 |  | REAR |  | -0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0021 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building pressure is slighly negative.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250