## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6000 | 6144 | 4800 | 4907 | 1200 | 1237 | 20% | 20.13%
RTU-2 | COOKLINE | 2400 | 2259 | 1900 | 2259 | 500 | 0 | 20.83% | 0%
RTU-3 | KITCHEN | 1200 | 1109 | 1100 | 1109 | 100 | 0 | 8.333% | 0%
MUA-1 | HOODS | [8 empty] | 2718 | 2662
EF-1 | HOODS | [10 empty] | 3600 | 3396
EF-2 | RESTROOM | [12 empty] | 200 | 701
TOTALS |  | 9600 | 9512 | 7800 | 8275 | 1800 | 1237 |  |  | 2718 | 2662 | 3600 | 3396 | 200 | 701
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4518 | 3899 |  | FRONT |  | -0.011 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3800 | 4097 |  | SIDE |  | -0.012 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 718 | -198 |  | REAR |  | -0.011 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.011333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
NO DESIGN OUTSIDE AIR CFM GIVEN FOR RTU-1. 20% USED.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0