## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-A-1 | SALES - A | 8000 | 7093 | 7350 | 6405 | 650 | 688 | 8.125% | 9.7%
RTU-A-2 | BAKERY | 1200 | 1191 | 946 | 921 | 254 | 270 | 21.17% | 22.67%
RTU-A-3 | SALES "A" | 8000 | 8023 | 7350 | 7416 | 650 | 607 | 8.125% | 7.566%
RTU-A-4 | SEAFOOD | 1200 | 1170 | 1000 | 956 | 200 | 214 | 16.67% | 18.29%
RTU-A-5 | DOCK | 5000 | 4964 | 4490 | 4455 | 510 | 509 | 10.2% | 10.25%
RTU-A-6 | CLEANING/BACK RESTROOMS | 1200 | 1288 | 1080 | 1161 | 120 | 127 | 10% | 9.86%
RTU-A-7 | CONFERENCE ROOM | 2000 | 2016 | 1700 | 1746 | 300 | 270 | 15% | 13.39%
RTU-A-8 | BREAKROOM | 2000 | 1828 | 1687 | 1533 | 313 | 295 | 15.65% | 16.14%
RTU-A-9 | DOCK | 2400 | 2402 | 2160 | 2168 | 240 | 234 | 10% | 9.742%
RTU-A-10 | DOCK | 3000 | 3070 | 2740 | 2802 | 260 | 268 | 8.667% | 8.73%
RTU-A-11 | DOCK | 4000 | 4023 | 3740 | 3782 | 260 | 241 | 6.5% | 5.991%
RTU-B-1 | SALES - B | 8000 | 7883 | 7285 | 7142 | 715 | 741 | 8.938% | 9.4%
RTU-B-2 | SALES B - DAIRY | 8000 | 8156 | 7240 | 7355 | 760 | 801 | 9.5% | 9.821%
RTU-B-3 | SALES B - PET | 8000 | 7879 | 7380 | 7252 | 620 | 627 | 7.75% | 7.958%
RTU-B-4 | SALES B - GROCERY | 8000 | 7986 | 7345 | 7352 | 655 | 634 | 8.188% | 7.939%
RTU-B-5 | SALES B - FROZEN FOODS | 8000 | 8090 | 7330 | 8090 | 670 | 0 | 8.375% | 0%
RTU-B-6 | SALES B - SCHOOL/KITCHEN | 8000 | 7822 | 7390 | 7208 | 610 | 614 | 7.625% | 7.85%
RTU-B-7 | BACKROOM | 4000 | 3966 | 3255 | 3215 | 745 | 751 | 18.62% | 18.94%
RTU-B-8 | GROCERY FREEZER/BACKROOM | 4000 | 4114 | 3210 | 3354 | 790 | 760 | 19.75% | 18.47%
RTU-C-1 | SALES C | 10000 | 9673 | 9180 | 8820 | 820 | 853 | 8.2% | 8.818%
RTU-C-2 | SALES C | 8000 | 8063 | 7430 | 7502 | 570 | 561 | 7.125% | 6.958%
RTU-C-3 | SALES C | 8000 | 8237 | 7360 | 7556 | 640 | 681 | 8% | 8.268%
RTU-C-4 | SALES C | 8000 | 8270 | 7090 | 7349 | 910 | 921 | 11.38% | 11.14%
RTU-C-5 | GAAMING | 4000 | 3945 | 3500 | 3458 | 500 | 487 | 12.5% | 12.34%
RTU-C-6 | CUSTOMER SERVICE | 4000 | 4085 | 3870 | 3969 | 130 | 116 | 3.25% | 2.84%
RTU-C-7 | PHARMACY | 2400 | 2450 | 1925 | 1950 | 475 | 500 | 19.79% | 20.41%
RTU-C-8 | VESTIBLE | 3000 | 2969 | 2795 | 2750 | 205 | 219 | 6.833% | 7.376%
RTU-D-1 | OFFICES | 3000 | 3161 | 2740 | 2893 | 260 | 268 | 8.667% | 8.478%
RTU-D-2 | SALES D | 4000 | 4035 | 3000 | 3074 | 1000 | 961 | 25% | 23.82%
RTU-D-3 | PICK-UP | 8000 | 7286 | 7425 | 6779 | 575 | 507 | 7.187% | 6.959%
RTU-D-4 | SEATING | 5000 | 4940 | 4260 | 4206 | 740 | 734 | 14.8% | 14.86%
RTU-D-5 | DELI | 4000 | 4261 | 3450 | 3728 | 550 | 533 | 13.75% | 12.51%
RTU-D-6 | TENANT | 3000 | 2956 | 2700 | 2670 | 300 | 286 | 10% | 9.675% | [6 empty] | TRUE | FALSE | FALSE
MUA-1 | DELI | [8 empty] | 2525 | 2772 |  |  |  |  | #DIV/0! | #DIV/0! | FALSE
EF-A1 | DELI | [10 empty] | 1400 | 1372 |  |  | #DIV/0!
EF-B1 | DELI | [10 empty] | 1400 | 1391
EF-2 | FRONT RESTROOMS | [12 empty] | 800 | 851
EF-3 | BACK RESTROOMS | [12 empty] | 1100 | 1160
EF-4 | BAKERY OVEN | [12 empty] | 900 | 918
EF-5 | BAKERY OVEN | [12 empty] | 900 | 884
EF-6 | DOCK ELECT. | [12 empty] | 700 | 765
EF-7 | FAMILY RESTROOMS | [12 empty] | 300 | 317
EF-8 | SEAFOOD | [12 empty] | 800 | 814
EF-9 | ACCOUNTING | [12 empty] | 75 | 80
EF-10 | GAMING | [12 empty] | 1825 | 1793
EF-11 | EXISTING RESTROOMS | [12 empty] | 300 | 299
EF-12 | WEST ELECTRICAL LARGE | [12 empty] | 700 | 697
EF-13 | WEST ELECTRICAL | [12 empty] | 300 | 310
TOTALS |  | 168400 | 167295 | 151403 | 151017 | 16997 | 16278 |  |  | 2525 | 2772 | 2800 | 2763 | 8700 | 8888
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 19522 | 19050 |  | FRONT
TOTAL EXHAUST |  | 11500 | 11651 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 8022 | 7399 |  | REAR
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
Open Business to many people walking in and out constanly to take building pressure.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0