## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KTICHEN | 9500 | 9036 | 7600 | 7032 | 1900 | 2004 | 20% | 22.18%
AC-2 | DINING A | 2500 | 3247 | 2000 | 2705 | 500 | 542 | 20% | 16.69%
AC-3 | DINING B | 4000 | 3836 | 3200 | 3005 | 800 | 831 | 20% | 21.66%
AC-4 | DINING B | 2750 | 2891 | 2250 | 2404 | 500 | 487 | 18.18% | 16.85%
AC-5 | PLAY AREA | 2000 | 1904 | 1600 | 1482 | 400 | 422 | 20% | 22.16%
AC-6 | BOH/OFFICE | 1200 | 1192 | 1000 | 972 | 200 | 220 | 16.67% | 18.46%
EF-1 | HD1 L+R | [10 empty] | 1912 | 1968
EF-2 | HOOD 3 | [10 empty] | 390 | 399
EF-3 | RESTROOM | [12 empty] | 500 | 582
EF-4 | HOOD 2 | [10 empty] | 701 | 677
TOTALS |  | 21950 | 22106 | 17650 | 17600 | 4300 | 4506 |  |  | 0 | 0 | 3003 | 3044 | 500 | 582
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4300 | 4506 |  | FRONT |  | 0.0102 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3503 | 3626 |  | SIDE |  | 0.0105 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 797 | 880 |  | REAR |  | 0.0086 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0097667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390