## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3310 | 3194 | 2596 | 2448 | 714 | 746 | 21.57% | 23.36%
RTU-2 | KITCHEN | 4000 | 4075 | 3200 | 3271 | 800 | 804 | 20% | 19.73%
MUA-1 | COOKLINE | [8 empty] | 1965 | 1986
KEF-1 | KITCHEN HOOD | [10 empty] | 2381 | 2329
CEF-1 | RESTROOM | [12 empty] | 100 | 88
CEF-2 | RESTROOM | [12 empty] | 100 | 100
EF-3 | TRASHROOM | [12 empty] | 200 | 197
TOTALS |  | 7310 | 7269 | 5796 | 5719 | 1514 | 1550 |  |  | 1965 | 1986 | 2381 | 2329 | 400 | 385
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3479 | 3536 |  | FRONT |  | 0.0023 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2781 | 2714 |  | SIDE |  | 0.0017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 698 | 822 |  | REAR |  | -0.0018 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00073333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0