## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3164 | 2850 | 2552 | 650 | 612 | 18.57% | 12%
RTU-2 | DINING | 4000 | 4063 | 3150 | 3240 | 850 | 823 | 21.25% | 21%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1817
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3385
EF-2 | RESTROOM | [12 empty] | 150 | 160
TOTALS |  | 7500 | 7227 | 6000 | 5792 | 1500 | 1435 |  |  | 1950 | 1817 | 3200 | 3385 | 150 | 160
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3450 | 3252 |  | FRONT |  | 0.0053 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3350 | 3545 |  | SIDE |  | 0.0088 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | -293 |  | REAR |  | 0.0027 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0056 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250