## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3957 | 3120 | 3039 | 880 | 918 | 22% | 23.2%
RTU-2 | KITCHEN | 2400 | 2470 | 2040 | 2122 | 360 | 348 | 15% | 14.09%
MUA-1 | COOKLINE | [8 empty] | 1630 | 1562
EF-1 | GRILL HD | [10 empty] | 1120 | 1127
EF-2 | OVEN HD | [10 empty] | 600 | 579
EF-3 | FRY HD | [10 empty] | 850 | 884
EF-4 | RESTROOM | [12 empty] | 75 | 73
EF-5 | RESTROOM | [12 empty] | 75 | 86
TOTALS |  | 6400 | 6427 | 5160 | 5161 | 1240 | 1266 |  |  | 1630 | 1562 | 2570 | 2590 | 150 | 159
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2870 | 2828 |  | FRONT |  | 0.0008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2720 | 2749 |  | SIDE |  | -0.0004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 150 | 79 |  | REAR |  | -0.0002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 6.6667e-05 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0