## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6975 | 6999 | 4975 | 4868 | 2000 | 2131 | 28.67% | 30.45%
RTU-2 | KITCHEN | 6575 | 6275 | 4575 | 4301 | 2000 | 1974 | 30.42% | 31.46%
KEF-1 | HHOOD 1 | [10 empty] | 1500 | 1463
KEF-2 | HHOOD 2 | [10 empty] | 1500 | 1545
KEF-3 | HHOOD 3 | [10 empty] | 350 | 347
EF-1 | RESTROOM | [12 empty] | 450 | 437
EF-2 | MOP ROOM | [12 empty] | 75 | 73
EF-3 | EMP.TOILET | [12 empty] | 75 | 77
TOTALS |  | 13550 | 13274 | 9550 | 9169 | 4000 | 4105 |  |  | 0 | 0 | 3350 | 3355 | 600 | 587
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4000 | 4105 |  | FRONT |  | 0.016 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3950 | 3942 |  | SIDE |  | 0.015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 163 |  | REAR |  | 0.014 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Due to missing speed controller KEF3 and EF1 could not both be running at time of pressure test. Pressure will be less positive when all exhaust fans are operational.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0