## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 9063 | 7000 | 7401 | 1750 | 1662 | 20% | 18.34%
AC-2 | DRIVE THRU | 5250 | 5278 | 4000 | 4088 | 1250 | 1190 | 23.81% | 22.55%
AC-3 | DINING | 5250 | 5125 | 4100 | 3902 | 1150 | 1223 | 21.9% | 23.86%
AC-4 | BOH | 1875 | 1985 | 1375 | 1524 | 500 | 461 | 26.67% | 23.22%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1781
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1478
EF-3 | RESTROOM | [12 empty] | 375 | 390
TOTALS |  | 21125 | 21451 | 16475 | 16915 | 4650 | 4536 |  |  | 0 | 0 | 3314 | 3259 | 375 | 390
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4536 |  | FRONT |  | 0.033 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3689 | 3649 |  | SIDE |  | 0.027 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 961 | 887 |  | REAR |  | 0.028 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.029333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390