## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9331 | 7500 | 7351 | 2000 | 1980 | 21.05% | 21.22%
AC-2 | DRIVE-THRU | 5600 | 5933 | 4200 | 4505 | 1400 | 1428 | 25% | 24.07%
AC-3 | RESTROOMS | 6400 | 6498 | 4800 | 4835 | 1600 | 1663 | 25% | 25.59%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1929
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1355
EF-3 | RESTROOM | [12 empty] | 700 | 701
TOTALS |  | 21500 | 21762 | 16500 | 16691 | 5000 | 5071 |  |  | 0 | 0 | 3315 | 3284 | 700 | 701
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5000 | 5071 |  | FRONT |  | 0.0015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4015 | 3985 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 985 | 1086 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00275 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390