## SUMMARY (2)
CORE
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FOOD SERVICE | 4500 | 4284 | 3800 | 3587 | 700 | 697 | 15.56% | 16.27%
RTU-2 | RETAIL | 3400 | 3428 | 3020 | 3044 | 380 | 384 | 11.18% | 11.2%
RTU-3 | FOH | 2400 | 2346 | 2200 | 2156 | 200 | 190 | 8.333% | 8.099%
EF-1 | RESTROOMS | [12 empty] | 375 | 381
EF-2 | BOH | [12 empty] | 400 | 385
EF-3 | TRASH | [12 empty] | 200 | 80
TOTALS |  | 10300 | 10058 | 9020 | 8787 | 1280 | 1271 |  |  | 0 | 0 | 0 | 0 | 975 | 846
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1280 | 1271 |  | FRONT |  | 0.0159 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 975 | 846 |  | SIDE |  | 0.0188 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 305 | 425 |  | REAR |  | 0.0117 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015467 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0