## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN/STORAGE | 2000 | 2247 | 1300 | 1635 | 700 | 612 | 35% | 27.24%
RTU-2 | DINING | 3400 | 3402 | 2300 | 2286 | 1100 | 1116 | 32.35% | 32.8%
RTU-3 | KITCHEN | 5000 | 5069 | 3365 | 4058 | 1635 | 1011 | 32.7% | 19.94%
KEF-1 | GRILL HOOD | [10 empty] | 1995 | 1759
KEF-2 | FRYER HOOD | [10 empty] | 1091 | 972
EF-4 | RESTROOMS | [12 empty] | 200 | 0
TOTALS |  | 10400 | 10718 | 6965 | 7979 | 3435 | 2739 |  |  | 0 | 0 | 3086 | 2731 | 200 | 0
[16 empty] | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 3435 | 2739 |  | FRONT |  | 0.0129
TOTAL EXHAUST |  | 3286 | 2731 |  | SIDE |  | 0.0119 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | TRUE
NET AIRFLOW |  | 149 | 8 |  | REAR |  | 0.0091
[5 empty] | AVERAGE |  | 0.0113
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0