## RTU-7
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-7 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 3.0 / 2634 |  | Horsepower / RPM | 1.50 / 1652
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 4.2 / |  | Rated Amperage / SF | 2.08 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6100 |  | Total CFM | 5185
Min OA CFM | 1415
Fan RPM | 1750 |  | Fan RPM | 1800
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 4.2 |  | RL Amperage | 2.08
Motor B.H.P. | (2) 2.85 |  | Motor B.H.P. | 1.28
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.9 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-8
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-8 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE313/DJE60/O/M/MV/R |  | Model Number | FWE313/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 7.5 / 1770 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 9.5 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 10000 |  | Total CFM | 8500
Min OA CFM | 2290
Fan RPM | 1770 |  | Fan RPM | 1200
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 9.5 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 5.0 |  | Motor B.H.P. | 1.68
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.4 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-9
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-9 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 3475 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 5.9 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7100 |  | Total CFM | 6035
Min OA CFM | 1370
Fan RPM | 2872 |  | Fan RPM | 1653
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 5.9 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.62 |  | Motor B.H.P. | 1.71
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-10
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-10 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 3475 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.3 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7200 |  | Total CFM | 6120
Min OA CFM | 1480
Fan RPM | 2893 |  | Fan RPM | 1668
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.3 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.69 |  | Motor B.H.P. | 1.76
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-11
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-11 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE263/DJE60/O/M/MV/R |  | Model Number | FWE263/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 8500 |  | Total CFM | 7225
Min OA CFM | 940
Fan RPM | 2109 |  | Fan RPM | 1124
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 4.14 |  | Motor B.H.P. | 1.84
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.3 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | .05

## RTU-12
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-12 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE252/DJE40/O/M/MV/R |  | Model Number | FWE252/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.7 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6600 |  | Total CFM | 5610
Min OA CFM | 2765
Fan RPM | 2307 |  | Fan RPM | 1735
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.7 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.1 |  | Motor B.H.P. | 1.48
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.0 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-13
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-13 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE354/DJE60/O/M/MV/R |  | Model Number | FWE354/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 7.5 / 1770 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 9.5 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 10000 |  | Total CFM | 8500
Min OA CFM | 4085
Fan RPM | 2256 |  | Fan RPM | 1130
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 9.5 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 5.09 |  | Motor B.H.P. | 1.68
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.5 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-14
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-14 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE313/DJE60/O/M/MV/R |  | Model Number | FWE313/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 8300 |  | Total CFM | 7055
Min OA CFM | 2860
Fan RPM | 2059 |  | Fan RPM | 1114
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.85 |  | Motor B.H.P. | 1.79
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-15
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-15 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE252/DJE40/O/M/MV/R |  | Model Number | FWE252/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 |  | Rated Amperage / SF | 2.78
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7200 |  | Total CFM | 6120
Min OA CFM | 2425
Fan RPM | 2386 |  | Fan RPM | 1668
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.42 |  | Motor B.H.P. | 1.76
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.0 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-16
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-16 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE285/DJE60/O/M/MV/R |  | Model Number | FWE285/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 9500 |  | Total CFM | 8050
Min OA CFM | 1280
Fan RPM | 2167 |  | Fan RPM | 1696
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 4.5 |  | Motor B.H.P. | 2.88
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.2 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-17
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-17 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 3475 |  | Horsepower / RPM | 3.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.3 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7500 |  | Total CFM | 6380
Min OA CFM | 800
Fan RPM | 2958 |  | Fan RPM | 1713
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.3 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 3.91 |  | Motor B.H.P. | 1.9
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-18
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-18 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 3475 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.3 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7200 |  | Total CFM | 6090
Min OA CFM | 580
Fan RPM | 2876 |  | Fan RPM | 1663
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.3 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.61 |  | Motor B.H.P. | 1.74
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.0 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-19
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-19 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 3.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7600 |  | Total CFM | 6440
Min OA CFM | 740
Fan RPM | 2460 |  | Fan RPM | 1724
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 3.74 |  | Motor B.H.P. | 1.93
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-20
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-20 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 1.5 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.08 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6200 |  | Total CFM | 5260
Min OA CFM | 1090
Fan RPM | 2672 |  | Fan RPM | 1667
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.08
Motor B.H.P. | (2) 2.97 |  | Motor B.H.P. | 1.32
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.0 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-21
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-21 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE183/DJE40/O/M/MV/R |  | Model Number | FWE183/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6300 |  | Total CFM | 5355
Min OA CFM | 1035
Fan RPM | 2692 |  | Fan RPM | 1537
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.04 |  | Motor B.H.P. | 1.39
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.0 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-25
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-25 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/M/MV/R |  | Model Number | FWE224/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 1.5 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.08 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6300 |  | Total CFM | 5355
Min OA CFM | 2250
Fan RPM | 2673 |  | Fan RPM | 1685
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.08
Motor B.H.P. | (2) 2.97 |  | Motor B.H.P. | 1.36
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.9 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-26
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-26 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE252/DJE40/O/M/MV/R |  | Model Number | FWE252/DJE40/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 3.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 8300 |  | Total CFM | 7055
Min OA CFM | 1600
Fan RPM | 2565 |  | Fan RPM | 1551
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 4.18 |  | Motor B.H.P. | 2.21
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.1 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-27
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-27 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE252/DJE60/O/M/MV/R |  | Model Number | FWE252/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.78 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 8600 |  | Total CFM | 310
Min OA CFM | 1795
Fan RPM | 2098 |  | Fan RPM | 1132
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 4.08 |  | Motor B.H.P. | 1.8
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.2 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-28
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-28 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE313/DJE60/O/M/MV/R |  | Model Number | FWE313/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 9200 |  | Total CFM | 7820
Min OA CFM | 3075
Fan RPM | 2160 |  | Fan RPM | 1.95
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 4.47 |  | Motor B.H.P. | 1.51
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.3 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-29
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-29 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE313/DJE60/O/M/MV/R |  | Model Number | FWE313/DJE60/O/M/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 7.5 / 1770 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 9.5 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 10000 |  | Total CFM | 8500
Min OA CFM | 2350
Fan RPM | 2887 |  | Fan RPM | 1130
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 9.5 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 5.74 |  | Motor B.H.P. | 1.68
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.4 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-41
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-41 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE224/DJE40/O/MV/R |  | Model Number | FWE224/DJE40/O/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 2.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 2.78
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 7200 |  | Total CFM | 6120
Min OA CFM | 1685
Fan RPM | 2421 |  | Fan RPM | 1115
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 2.78
Motor B.H.P. | (2) 3.58 |  | Motor B.H.P. | 1.4
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.2 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-42
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-42 |  | Area:
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | FWE263/DJE40/O/MV/R |  | Model Number | FWE263/DJE40/O/MV/R
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 3 / 25X16X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 5.0 / 1750 |  | Horsepower / RPM | 3.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 6.6 / |  | Rated Amperage / SF | 3.85 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 9100 |  | Total CFM | 7735
Min OA CFM | 495
Fan RPM | 2186 |  | Fan RPM | 1649
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 6.6 |  | RL Amperage | 3.85
Motor B.H.P. | (2) 4.62 |  | Motor B.H.P. | 2.65
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.5 |  | Total SP | 0.6
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 0.5

## RTU-HV-1
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-HV-1 |  | Area: DIESEL 511
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | DJX100/HRW2400/O/MV |  | Model Number | DJX100/HRW2400/O/MV
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 12 / 24X20X2 |  | No. Return Filters / Size | 8 / 24x24x2
No. Final Filters / Size | 12 / 24X20X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 10.0 / 1750 |  | Horsepower / RPM | (2) 6.7 / 1450
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 12.3 / |  | Rated Amperage / SF | (2) 6.2 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 12835 |  | Total CFM | 15831
Min OA CFM | 1520
Fan RPM | 1908 |  | Fan RPM | 1355
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 12.3 |  | RL Amperage | (2) 6.2
Motor B.H.P. | (2) 8.37 |  | Motor B.H.P. | (2) 5.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 5.0 |  | Total SP | 2.8
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 1.0

## RTU-HV-1 SGRD
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-HV-1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1 | 511 | G1 | 24X10 | 535 |  |  | 0
1-2 | 511 | G1 | 24X10 | 535 |  |  | 0
1-3 | 511 | G1 | 24X10 | 805 |  |  | 0
1-4 | 511 | G1 | 24X10 | 805 |  |  | 0
1-5 | 511 | G1 | 24X10 | 805 |  |  | 0
1-6 | 511 | G1 | 24X10 | 805 |  |  | 0
1-7 | 511 | G1 | 24X10 | 805 |  |  | 0
1-8 | 511 | G1 | 24X10 | 535 |  |  | 0
1-9 | 511 | G1 | 24X10 | 535 |  |  | 0
1-10 | 511 | G1 | 24X10 | 665 |  |  | 0
1-11 | 511 | G1 | 24X10 | 665 |  |  | 0
1-12 | 511 | G1 | 24X10 | 665 |  |  | 0
1-13 | 511 | G1 | 24X10 | 535 |  |  | 0
1-14 | 511 | G1 | 24X10 | 535 |  |  | 0
1-15 | 511 | G1 | 24X10 | 665 |  |  | 0
1-16 | 511 | G1 | 24X10 | 665 |  |  | 0
1-17 | 511 | G1 | 24X10 | 665 |  |  | 0
1-18 | 511 | G1 | 24X10 | 805 |  |  | 0
1-19 | 511 | G1 | 24X10 | 805 |  |  | 0
|  |  |  | 12835 |  | 0 | 0

## RTU-HV-2
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-HV-2 |  | Area: CONSTRUCTION 744, ELECT. LAB 745
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ENGINEERED AIR |  | Manufacturer | ENGINEERED AIR
Model Number | DJX100/HRW2400/O/MV |  | Model Number | DJX100/HRW2400/O/MV
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24x24x2 |  | No. Return Filters / Size | 8 / 24x24x2
No. Final Filters / Size | 8 / 24x24x12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | (2) 10.0 / 1750 |  | Horsepower / RPM | (2) 6.7 / 1450
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | (2) 12.3 / |  | Rated Amperage / SF | (2) 6.2 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 14230 |  | Total CFM | 14331
Min OA CFM | 1520
Fan RPM | 2210 |  | Fan RPM | 1289
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | (2) 12.3 |  | RL Amperage | (2) 6.2
Motor B.H.P. | (2) 7.53 |  | Motor B.H.P. | (2) 4.6
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.7 |  | Total SP | 2.7
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.5 |  | Total ESP | 1.0

## RTU-HV-2 SGRD
National TAB
Project: Scarlet Oaks RTU Replacement
Address: 3254 Kemper Rd. Cincinnati, OH
Asset: RTU-HV-2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-1 | 744 | G1 | 24X12 | 700 |  |  | 0
2-2 | 744 | G1 | 24X12 | 700 |  |  | 0
2-3 | 744 | G1 | 24X12 | 700 |  |  | 0
2-4 | 744 | G1 | 24X12 | 700 |  |  | 0
2-5 | 745 | G1 | 24X12 | 680 |  |  | 0
2-6 | 745 | G1 | 24X12 | 510 |  |  | 0
2-7 | 745 | G1 | 24X12 | 510 |  |  | 0
2-8 | 745 | G1 | 24X12 | 510 |  |  | 0
2-9 | 745 | G1 | 24X12 | 510 |  |  | 0
2-10 | 745 | G1 | 24X12 | 510 |  |  | 0
2-11 | 744 | G1 | 24X12 | 700 |  |  | 0
2-12 | 744 | G1 | 24X12 | 700 |  |  | 0
2-13 | 744 | G1 | 24X12 | 700 |  |  | 0
2-14 | 745 | G1 | 24X10 | 500 |  |  | 0
2-15 | 745 | G1 | 24X10 | 500 |  |  | 0
2-16 | 745 | G1 | 24X10 | 500 |  |  | 0
2-17 | 745 | G1 | 24X10 | 500 |  |  | 0
2-18 | 744 | G1 | 24X12 | 700 |  |  | 0
2-19 | 744 | G1 | 24X12 | 700 |  |  | 0
2-20 | 745 | G1 | 24X10 | 500 |  |  | 0
2-21 | 745 | G1 | 24X10 | 500 |  |  | 0
2-22 | 745 | G1 | 24X10 | 500 |  |  | 0
2-23 | 745 | G1 | 24X10 | 500 |  |  | 0
2-24 | 744 | G1 | 24X12 | 700 |  |  | 0
|  |  |  | 14230 |  | 0 | 0