## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | STORAGE | 1750 | 1796 | 1600 | 1649 | 150 | 147 | 8.571% | 8.185%
RTU-2 | WEST SALES | 2800 | 2931 | 2450 | 2561 | 350 | 370 | 12.5% | 12.62%
RTU-3 | EAST SALES | 2800 | 2777 | 2450 | 2417 | 350 | 360 | 12.5% | 12.96%
RTU-4 | SOUTH SALES | 3500 | 3624 | 3100 | 3207 | 400 | 417 | 11.43% | 11.51%
RTU-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-7 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-8 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-9 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-10 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-11 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-12 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-13 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-14 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-15 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-16 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
MUA-1
MUA-1
EF-1 | RESTROOM | [12 empty] | 75 | 40
EF-2 | RESTROOM | [12 empty] | 75 | 39
EF-3
EF-4
EF-5
EF-6
EF-1
EF-2
EF-3
EF-4
EF-5
EF-6
TOTALS |  | 10850 | 11128 | 9600 | 9834 | 1250 | 1294 |  |  | 0 | 0 | 0 | 0 | 150 | 79
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1250 | 1294 |  | FRONT |  | 0.0165 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 150 | 79 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1100 | 1215 |  | REAR |  | 0.0102 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01335 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0