## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 |  | 6375 | 0 | 1750 |  | 21.54% | #DIV/0!
AC-2 | DRIVE THRU | 5250 | 5431 | 4100 | 4289 | 1150 | 1142 | 21.9% | 21.03%
AC-3 | DINING | 5250 | 5476 | 4000 | 4281 | 1250 | 1195 | 23.81% | 21.82%
AC-4 | BOH | 2100 | 2179 | 1600 | 1688 | 500 | 491 | 23.81% | 22.53%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0
EF-1 | HD 1 | [10 empty] | 1913 | 1952
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1454
EF3 | RESTROOMS | [12 empty] | 300 | 292
EF 4 | RESTROOMS
EF-3 | RESTROOMS
TOTALS |  | 20725 | 13086 | 16075 | 10258 | 4650 | 2828 |  |  | 0 | 0 | 3315 | 3406 | 300 | 292
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4650 | 2828 |  | FRONT |  | -0.003 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3615 | 3698 |  | SIDE |  | -0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1035 | -870 |  | REAR |  | -0.005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390