## RTU1
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 |  | Area: ACADEMIC WEST
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | INNOVENT |  | Manufacturer | INNOVENT
Model Number | CAHU-50000-AC-460 |  | Model Number | CAHU-50000-AC-460
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 28 / 20X16X2 |  | No. Pre Filters / Size
No. Pre Filters / Size | 14 / 25X16X2 |  | No. Pre Filters / Size
No. Pre Filters / Size
No. Final Filters / Size | 28 / 20X16X4
No. Final Filters / Size | 14 / 25X16X4
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 4 @ 20.0 / 1800 |  | Horsepower / RPM | 2 @ 10.0 / 1160
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 50000 |  | Total CFM | 48302
Min OA CFM | 10000 |  | Fan RPM | 1160
Return CFM | 40000 |  | Operating HZ
Fan RPM | 2076 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage
RL Voltage | 460 |  | Motor B.H.P. | 18.2
RL Amperage
Motor B.H.P. | 69.36
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 6.29 |  | Total SP | 1.3
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 3.50 |  | Total ESP | 1.213

## RTU1 RETURN
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R1-1 | 505 |  | 24X18 | 1485 |  |  | 0
R1-2 | 456 |  | 24X18 | 925 |  |  | 0
R1-3 | 405 |  | 24X18 | 2180 |  |  | 0
R1-4 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-5 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-6 | 461 | LR1 | 6'-0" | 1200 |  |  | 0
R1-7 | 461 | LR1 | 2'-0" | 400 |  |  | 0
R1-8 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-9 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-10 | 461 | R2 | 22X22 | 1000 |  |  | 0
R1-11 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-12 | 461 | LR1 | 5'-0" | 1000 |  |  | 0
R1-13 | 356 |  | 22X18 | 700 |  |  | 0
R1-14 | 352 |  | 22X20 | 700 |  |  | 0
R1-15 | 360 |  | 16X14 | 700 |  |  | 0
R1-16 | 357 |  | 16X14 | 900 |  |  | 0
R1-17 | 361 |  | 30X22 | 4925 |  |  | 0
R1-18 | 220 |  | 30X22 | 3725 |  |  | 0
R1-19 | 200 |  | 78X38 | 17800 |  |  | 0
R1-20 | 150 | R1 | 22X22 | 800 |  |  | 0
R1-21 | 150 | R1 | 22X22 | 800 |  |  | 0
R1-22 | 159 |  | 34X24 | 3950 |  |  | 0
|  |  |  | 48190 |  | 0 | 0

## RTU2
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 |  | Area: ACADEMIC CENTER
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | RPS080D |  | Model Number | RPS080D
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 4 / 12X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size
No. Pre Filters / Size
No. Final Filters / Size | 12 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 40.0 / |  | Horsepower / RPM | 20.0 /
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 46.0 |  | Rated Amperage / SF | 23.5
Drive Data |  |  | Drive Data
Motor Sheave Size / Bore |  |  | Motor Sheave Size / Bore
Fan Sheave Size / Bore |  |  | Fan Sheave Size / Bore
Belt CL Distance |  |  | Belt CL Distance
No. Belts / Size |  |  | No. Belts / Size
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 28000 |  | Total CFM | 2800
Min OA CFM | 6500 |  | Fan RPM | 782
Return CFM | 21500 |  | Operating HZ
Fan RPM | 1320 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage | 23.5
RL Voltage | 460 |  | Motor B.H.P. | 15.68
RL Amperage | 46.0
Motor B.H.P. | 32.28
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 5.10 |  | Total SP | 2.0
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.50 |  | Total ESP | 2.0

## RTU2 RETURN
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R2-1 | 517 |  | 20X18 | 1000 |  |  | 0
R2-2 | 519 |  | 22X18 | 1100 |  |  | 0
R2-3 | 505 |  | 44X22 | 6200 |  |  | 0
R2-4 | 526 |  |  | 1200 |  |  | 0
R2-5 | 420 |  | 16X12 | 650 |  |  | 0
R2-6 | 418 |  | 22X16 | 400 |  |  | 0
R2-7 | 416 |  | 30X18 | 400 |  |  | 0
R2-8 | 421 |  | 20X18 | 800 |  |  | 0
R2-9 | 417 |  | 20X18 | 800 |  |  | 0
R2-10 | 405 |  | 34X18 | 3300 |  |  | 0
R2-11 | 325 |  | 2420 | 700 |  |  | 0
R2-12 | 319 |  | 22X18 | 700 |  |  | 0
R2-13 | 305 |  | 24X18 | 3260 |  |  | 0
R2-14 | 320 |  | 30X18 | 1970 |  |  | 0
R2-15 | 206 |  | 24X20 | 2225 |  |  | 0
|  |  |  | 24705 |  | 0 | 0

## RTU3
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 |  | Area: ACADEMIC EAST
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS061E |  | Model Number | MPS061E
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 4 / 12X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size
No. Pre Filters / Size
No. Final Filters / Size | 8 / 24X24X12
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 30.0 / |  | Horsepower / RPM | 5.0 /
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 35.0 / |  | Rated Amperage / SF | 6.6 /
Drive Data |  |  | Drive Data
Motor Sheave Size / Bore |  |  | Motor Sheave Size / Bore
Fan Sheave Size / Bore |  |  | Fan Sheave Size / Bore
Belt CL Distance |  |  | Belt CL Distance
No. Belts / Size |  |  | No. Belts / Size
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 17500 |  | Total CFM | 16000
Min OA CFM | 5200 |  | Fan RPM
Return CFM | 12300 |  | Operating HZ
Fan RPM | 1022 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage | 6.6
RL Voltage | 460 |  | Motor B.H.P.
RL Amperage | 35.0
Motor B.H.P. | 23.0
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 5.10 |  | Total SP
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 3.0 |  | Total ESP

## RTU3 RETURN
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R3-1 | 529 |  | 22X18 | 1000 |  |  | 0
R3-2 | 505 |  | 28X20 | 1750 |  |  | 0
R3-3 | 534 |  | 22X18 | 1000 |  |  | 0
R3-4 | 533 |  | 22X20 | 1200 |  |  | 0
R3-5 | 532 |  | 22X18 | 1000 |  |  | 0
R3-6 | 505 |  | 34X22 | 1200 |  |  | 0
R3-7 | 431 |  | 20X18 | 1100 |  |  | 0
R3-8 | 405 |  | 18X14 | 1200 |  |  | 0
R3-9 | 432 |  | 20X18 | 800 |  |  | 0
R3-10 | 427 |  | 20X18 | 800 |  |  | 0
R3-11 | 423 |  | 16X14 | 500 |  |  | 0
R3-12 | 428 |  | 16X14 | 800 |  |  | 0
R3-13 | 339 |  | 20X18 | 1000 |  |  | 0
R3-14 | 305 |  | 20X18 | 1200 |  |  | 0
R3-15 [1] | 338 |  | 20X18
R3-16 | 335 |  | 20X18 | 800 |  |  | 0
R3-17 | 331 |  | 16X14 | 175 |  |  | 0
R3-18 | 330 |  | 16X14 | 400 |  |  | 0
R3-19 | 334 |  | 20X18 | 800 |  |  | 0
|  |  |  | 16725 |  | 0 | 0
NOTES: | [1] NO CFM LISTED ON DRAWING

## RTU4
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU4 |  | Area: GYMNASIUM
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS040F |  | Model Number | MPS040F
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 4 / 18X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 15.0 / |  | Horsepower / RPM | 1.0 /
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 17.7 / |  | Rated Amperage / SF | 2.0 /
Drive Data
Motor Sheave Size / Bore
Fan Sheave Size / Bore
Belt CL Distance
No. Belts / Size
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 12800 |  | Total CFM | 14000
Min OA CFM | 4000 |  | Fan RPM
Return CFM | 8800 |  | Operating HZ
Fan RPM | 1268 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage | 2.0
RL Voltage | 460 |  | Motor B.H.P.
RL Amperage | 17.7
Motor B.H.P. | 10.8
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.83 |  | Total SP
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.00 |  | Total ESP

## RTU-4 SUPPLY
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU4 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
4-1 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-2 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-3 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-4 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-5 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-6 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-7 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-8 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-9 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-10 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-11 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
4-12 | OPEN [1] | R7 | 30X8 | 1000 |  |  | 0
|  |  |  | 12000 |  | 0 | 0
NOTES: | [1] OPEN TO BELOW (GYM)

## RTU4 RETURN
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU4 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R4-1 [1] | GYM |  | 40X24 |  |  |  | #DIV/0!
R4-2 [1] | GYM |  | 40X24 |  |  |  | #DIV/0!
|  |  |  | 0 |  | 0 | #DIV/0!
NOTES: | [1] NO CFM LISTED ON DRAWING

## RTU5
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU5 |  | Area: COMMUNITY SERVICES
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | DPS015A |  | Model Number | DPS015A
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 18X24X2 |  | No. Pre Filters / Size
No. Final Filters / Size | 6 / 18X24X4 |  | No. Pre Filters / Size
No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 8.0 / |  | Horsepower / RPM | 8.0 /
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 6.8 / |  | Rated Amperage / SF | 7.3 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 6000 |  | Total CFM | 6000
Min OA CFM | 1000 |  | Fan RPM | 1902
Return CFM | 5000 |  | Operating HZ
Fan RPM | 2411 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage | 7.3
RL Voltage | 460 |  | Motor B.H.P. | 1.85
RL Amperage | 6.8
Motor B.H.P. | 4.86
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.28 |  | Total SP
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.50 |  | Total ESP | 0.50

## RTU6
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU6 |  | Area: KITCHEN/LOCKERS
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | VALENT |  | Manufacturer | VALENT
Model Number | VXE-312-74-30L-30I-O |  | Model Number | VXE-312-74-30L-30I-O
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 20X24X2 |  | No. Pre Filters / Size | 8 / 20X24X2
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size | 4 / 16X20X2 |  | No. Pre Filters / Size
No. Final Filters / Size | 8 / 20X20X2
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 7.5 / 1770 |  | Horsepower / RPM | 1.0 / 1760
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 9000 |  | Total CFM | 4400
Min OA CFM | 9000 |  | Fan RPM | 1190
Return CFM | 0 |  | Operating HZ
Fan RPM | 1622 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage
RL Voltage | 460 |  | Motor B.H.P. | 0.58
RL Amperage
Motor B.H.P. | 4.1
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.036 |  | Total SP | 1.05
System S.P. Set Point
CW Coil P.D.
HW Coil P.D. |  |  | Heat Wheel P.D.
Final Filters P.D. |  |  | HW Coil P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Heat Wheel P.D. |  |  | Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.00 |  | Total ESP | 0.50

## RTU6 RETURN
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU6 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R6-1 | 125 |  | 28X20 | 2800 |  |  | 0
R6-2 | 121 |  | 20X16 | 1250 |  |  | 0
R6-3 | 114 | R1 | 22X22 | 2000 |  |  | 0
|  |  |  | 6050 |  | 0 | 0

## RTU-1 VAV's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-1 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU1-1-01 | 164 | REHEAT | SINGLE | 10 | 700 |  | 450
RTU1-1-02 | 163 | REHEAT | SINGLE | 10 | 600 |  | 375
RTU1-1-03 | OPEN | REHEAT | SINGLE | 10 | 500 |  | 325
RTU1-1-04 | 160 | REHEAT | SINGLE | 6 | 230 |  | 150
RTU1-1-05 | 161 | REHEAT | SINGLE | 10 | 725 |  | 600
RTU1-1-06 | 159 | REHEAT | SINGLE | 8 | 400 |  | 150
RTU1-1-07 | 154 | REHEAT | SINGLE | 10 | 800 |  | 325
RTU1-1-08 | 101 | REHEAT | SINGLE | 10 | 750 |  | 450
RTU1-1-09 | 103 | REHEAT | SINGLE | 16 | 1700 |  | 850
RTU1-1-10 | 150 | REHEAT | SINGLE | 16 | 2110 |  | 1400
RTU1-1-10 [2] | 152 | REHEAT | SINGLE | 8 | 250 |  | 200
RTU1-2-01 | 220 | REHEAT | SINGLE | 16 | 2600 |  | 1250
RTU1-2-02 | 212 | REHEAT | SINGLE | 12 | 1125 |  | 700
RTU1-2-03 | OPEN [1] | REHEAT | SINGLE | 16 | 2860 |  | 1200
RTU1-2-04 | OPEN [1] | REHEAT | SINGLE | 16 | 2600 |  | 1200
RTU1-2-05 | OPEN [1][3] | REHEAT | SINGLE | 16 | 1500 |  | 600
RTU1-2-06 | 200 | REHEAT | SINGLE | 16 | 2200 |  | 1400
RTU1-2-07 | 200 | REHEAT | SINGLE | 10 | 750 |  | 450
RTU1-2-08 | OPEN [1] | REHEAT | SINGLE | 16 | 2600 |  | 1200
RTU1-2-09 | OPEN [1] | REHEAT | SINGLE | 16 | 2275 |  | 800
RTU1-2-10 | 202 | REHEAT | SINGLE | 12 | 950 |  | 950
RTU1-2-11 | OPEN [1] | REHEAT | SINGLE | 16 | 2080 |  | 1200
NOTES: | [1] OPEN TO BELOW (DINING)
[2] DUPLICATE VAV TAG
[3] VAV DESIGN MAX IS 1500 CFM, DIFFUSER TOTAL IS 3120 CFM
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU-1 VAV's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-1 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU1-3-01 | 366 | REHEAT | SINGLE | 10 | 650 |  | 350
RTU1-3-02 | 364 | REHEAT | SINGLE | 6 | 125 |  | 100
RTU1-3-03 | 362 | REHEAT | SINGLE | 6 | 150 |  | 100
RTU1-3-04 | 361 | REHEAT | SINGLE | 16 | 2000 |  | 1100
RTU1-3-05 | 356 | REHEAT | SINGLE | 12 | 800 |  | 580
RTU1-3-06 | 357 | REHEAT | SINGLE | 12 | 1000 |  | 600
RTU1-3-07 | 360 | REHEAT | SINGLE | 10 | 700 |  | 600
RTU1-3-08 | 352 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU1-4-01 | 461 | REHEAT | SINGLE | 10 | 800 |  | 450
RTU1-4-02 | 405 | REHEAT | SINGLE | 16 | 2180 |  | 1200
RTU1-4-03 | 456 | REHEAT | SINGLE | 10 | 675 |  | 400
RTU1-4-04 | 454 | REHEAT | SINGLE | 6 | 150 |  | 100
RTU1-4-05 | 452 | REHEAT | SINGLE | 6 | 100 |  | 100
RTU1-5-01 | 560 | REHEAT | SINGLE | 14 | 1485 |  | 825
RTU1-5-02 | OPEN [1] | REHEAT | SINGLE | 16 | 3200 |  | 1800
RTU1-5-03 | OPEN [1] | REHEAT | SINGLE | 16 | 2800 |  | 1600
RTU1-5-04 | OPEN [1] | REHEAT | SINGLE | 16 | 2400 |  | 800
NOTES: | [1] OPEN TO BELOW (MEDIA CENTER)
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU1 SGRD's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1-01-1 | 164 | LD2 | 6'-0" | 250 |  |  | 0
1-1-01-2 | 164 | LD2 | 4'-0" | 150 |  |  | 0
1-1-01-3 | 164 | LD2 | 4'-0" | 150 |  |  | 0
1-1-01-4 | 164 | LD2 | 4'-0" | 150 |  |  | 0
RTU1-1-01 |  |  |  | 700 |  | 0 | 0
1-1-02-1 | 163 | LD2 | 6'-0" | 300 |  |  | 0
1-1-02-2 | 163 | LD2 | 6'-0" | 300 |  |  | 0
RTU1-1-02 |  |  |  | 600 |  | 0 | 0
1-1-03-1 | OPEN | LD1 | 4'-0" | 125 |  |  | 0
1-1-03-2 | OPEN | LD1 | 4'-0" | 125 |  |  | 0
1-1-03-3 | OPEN | LD1 | 4'-0" | 125 |  |  | 0
RTU1-1-03 |  |  |  | 375 |  | 0 | 0
1-1-04-1 | 160 | LD1 | 4'-0" | 115 |  |  | 0
1-1-04-2 | 160 | LD1 | 4'-0" | 115 |  |  | 0
RTU1-1-04 |  |  |  | 230 |  | 0 | 0
1-1-05-1 | 161 | D1 | 10 | 250 |  |  | 0
1-1-05-2 | 161 | D1 | 10 | 250 |  |  | 0
1-1-05-3 | 161 | LD2 | 6'-0" | 225 |  |  | 0
RTU1-1-05 |  |  |  | 725 |  | 0 | 0
1-1-06-1 | 159 | D1 | 6 | 100 |  |  | 0
1-1-06-2 | 157 | D1 | 6 | 100 |  |  | 0
1-1-06-3 [1] | 155 | [5 empty] | #DIV/0!
RTU1-1-06 |  |  |  | 200 |  | 0 | 0
1-1-07-1 | 154 | LD1 | 4'-0" | 200 |  |  | 0
1-1-07-2 | 154 | D1 | 8 | 200 |  |  | 0
1-1-07-3 | 154 | LD1 | 4'-0" | 200 |  |  | 0
1-1-07-4 | 154 | LD1 | 4'-0" | 200 |  |  | 0
RTU1-1-07 |  |  |  | 800 |  | 0 | 0
1-1-08-1 | 101 | LD4 | 4'-0" | 250 |  |  | 0
1-1-08-2 | 101 | LD4 | 4'-0" | 250 |  |  | 0
1-1-08-3 | 101 | LD4 | 4'-0" | 250 |  |  | 0
RTU1-1-08 |  |  |  | 750 |  | 0 | 0
NOTES: | [1] NO DIFFUSER TYPE OR CFM ON DRAWING

## RTU1 SGRD's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1-09-1 | 102 | LD1 | 6'-0" | 350 |  |  | 0
1-1-09-2 | 103 | LD1 | 6'-0" | 300 |  |  | 0
1-1-09-3 | 103 | LD1 | 6'-0" | 300 |  |  | 0
1-1-09-4 | 105 | LD4 | 4'-0" | 250 |  |  | 0
1-1-09-5 | 105 | LD4 | 4'-0" | 250 |  |  | 0
1-1-09-6 | 105 | LD4 | 4'-0" | 250 |  |  | 0
RTU1-1-09 |  |  |  | 1700 |  | 0 | 0
1-1-10-1 | 150 | D1 | 8 | 175 |  |  | 0
1-1-10-2 | 150 | D1 | 8 | 175 |  |  | 0
1-1-10-3 | 150 | LD4 | 10 | 250 |  |  | 0
1-1-10-4 | 150 | LD4 | 10 | 250 |  |  | 0
1-1-10-5 | 150 | D1 | 8 | 175 |  |  | 0
1-1-10-6 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-7 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-8 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-9 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-10 | 150 | D1 | 8 | 175 |  |  | 0
1-1-10-11 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-12 | 150 | LD2 | 4'-0" | 130 |  |  | 0
1-1-10-13 | 150 | LD2 | 4'-0" | 130 |  |  | 0
RTU1-1-10 |  |  |  | 2110 |  | 0 | 0
1-1-10-1 | 152 | D2 | 10 | 250 |  |  | 0
RTU1-1-10 [2] |  |  |  | 250 |  | 0 | 0
NOTES: | [1] NO DIFFUSER TYPE OR CFM ON DRAWING
[2] DUPLICATE VAV TAG

## RTU1 SGRD's (3)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-2-01-1 | 219 | D1 | 6 | 75 |  |  | 0
1-2-01-2 | 220 | D1 | 8 | 175 |  |  | 0
1-2-01-3 | 220 | D1 | 8 | 175 |  |  | 0
1-2-01-4 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-5 | 220 | D1 | 8 | 175 |  |  | 0
1-2-01-6 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-7 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-8 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-9 | 220 | D1 | 8 | 175 |  |  | 0
1-2-01-10 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-11 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-12 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-13 | 220 | D1 | 8 | 175 |  |  | 0
1-2-01-14 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-15 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-16 | 220 | L2 | 4'-0" | 150 |  |  | 0
1-2-01-17 | 220 | L2 | 4'-0" | 150 |  |  | 0
RTU1-2-01 |  |  |  | 2600 |  | 0 | 0
1-2-02-1 | 212 | D1 | 8 | 225 |  |  | 0
1-2-02-2 | 212 | D1 | 8 | 225 |  |  | 0
1-2-02-3 | 212 | D1 | 8 | 225 |  |  | 0
1-2-02-4 | 212 | D1 | 8 | 225 |  |  | 0
1-2-02-5 | 212 | D1 | 8 | 225 |  |  | 0
RTU1-2-02 |  |  |  | 1125 |  | 0 | 0
1-2-03-1 | OPEN [1] | LD1 | 4'-0" | 520 |  |  | 0
1-2-03-2 | OPEN [1] | LD1 | 4'-0" | 520 |  |  | 0
1-2-03-3 | OPEN [1] | LD1 | 4'-0" | 520 |  |  | 0
1-2-03-4 | OPEN [1] | LD1 | 4'-0" | 520 |  |  | 0
1-2-03-5 | OPEN [1] | LD5 | 6'-0" | 780 |  |  | 0
RTU1-2-03 |  |  |  | 2860 |  | 0 | 0
1-2-04-1 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-04-2 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-04-3 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-04-4 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-04-5 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
RTU1-2-04 |  |  |  | 2600 |  | 0 | 0
NOTES: | [1] OPEN TO BELOW (DINING)

## RTU1 SGRD's (4)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-2-05-1 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
1-2-05-2 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
1-2-05-3 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
1-2-05-4 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
1-2-05-5 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
1-2-05-6 | OPEN [1] | LD6 | 4'-0" | 520 |  |  | 0
RTU1-2-05 [3] |  |  |  | 3120 |  |  | 0
#DIV/0!
1-2-06-1 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-2 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-3 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-4 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-5 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-6 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-7 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-8 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-9 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-10 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-11 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-12 | 200 | LD1 | 4'-0" | 150 |  |  | 0
1-2-06-13 | 200 | LD1 | 4'-0" | 200 |  |  | 0
1-2-06-14 | 200 | LD1 | 4'-0" | 200 |  |  | 0
RTU1-2-06 |  |  |  | 2200 |  | 0 | 0
1-2-07-1 | 200 | LD5 | 4'-0" | 375 |  |  | 0
1-2-07-2 | 200 | LD5 | 4'-0" | 375 |  |  | 0
RTU1-2-07 |  |  |  | 750 |  | 0 | 0
1-2-08-1 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-08-2 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-08-3 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-08-4 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-08-5 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
RTU1-2-08 |  |  |  | 2600 |  | 0 | 0
NOTES: | [1] OPEN TO BELOW (DINING)
[3] VAV DESIGN MAX IS 1500 CFM, DIFFUSER TOTAL IS 3120 CFM

## RTU1 SGRD's (5)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-2-09-1 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-2 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-3 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-4 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-5 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-6 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-7 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-8 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-9 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-10 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-11 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-12 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
1-2-09-13 | OPEN [1] | LD1 | 4'-0" | 175 |  |  | 0
RTU1-2-09 |  |  |  | 2275 |  | 0 | 0
1-2-10-1 | E202 | R5 | 12X10 | 250 |  |  | 0
1-2-10-2 | 202 | D2 | 12 | 350 |  |  | 0
1-2-10-3 | 203 | D2 | 12 | 350 |  |  | 0
RTU1-2-10 |  |  |  | 950 |  | 0 | 0
1-2-11-1 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-11-2 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-11-3 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
1-2-11-4 | OPEN [1] | LD5 | 4'-0" | 520 |  |  | 0
RTU1-2-11 |  |  |  | 2080 |  | 0 | 0
1-3-01-1 | 366 | D1 | 12 | 325 |  |  | 0
1-3-01-2 | 366 | D1 | 12 | 325 |  |  | 0
RTU1-3-01 |  |  |  | 650 |  | 0 | 0
1-3-02-1 | 364 | D1 | 8 | 125 |  |  | 0
RTU1-3-02 |  |  |  | 125 |  | 0 | 0
1-3-03-1 | 362 | D1 | 8 | 150 |  |  | 0
RTU1-3-03 |  |  |  | 150 |  | 0 | 0
NOTES: | [1] OPEN TO BELOW (DINING)

## RTU1 SGRD's (6)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-3-04-1 | 361 | D1 | 8 | 150 |  |  | 0
1-3-04-2 | 361 | D1 | 8 | 150 |  |  | 0
1-3-04-3 | 361 | D1 | 8 | 150 |  |  | 0
1-3-04-4 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-5 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-6 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-7 | 361 | D1 | 8 | 150 |  |  | 0
1-3-04-8 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-9 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-10 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-11 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-12 | 361 | LD1 | 4'-0" | 150 |  |  | 0
1-3-04-13 | 361 | D1 | 8 | 150 |  |  | 0
1-3-04-14 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-15 | 361 | LD2 | 4'-0" | 100 |  |  | 0
1-3-04-16 | 361 | LD2 | 4'-0" | 100
1-3-04-17 | 361 | LD2 | 4'-0" | 100 |  |  | 0
RTU1-3-04 |  |  |  | 2000 |  | 0 | 0
1-3-05-1 | 356 | D1 | 8 | 200 |  |  | 0
1-3-05-2 | 356 | D1 | 8 | 200 |  |  | 0
1-3-05-3 | 356 | D1 | 8 | 200 |  |  | 0
1-3-05-4 | 356 | D1 | 8 | 200 |  |  | 0
RTU1-3-05 |  |  |  | 800 |  | 0 | 0
1-3-06-1 | 357 | D1 | 8 | 200 |  |  | 0
1-3-06-2 | 357 | D1 | 8 | 200 |  |  | 0
1-3-06-3 | 357 | D1 | 8 | 200 |  |  | 0
1-3-06-4 | 357 | D1 | 8 | 200 |  |  | 0
1-3-06-5 | 357 | D1 | 8 | 200 |  |  | 0
RTU1-3-06 |  |  |  | 1000 |  | 0 | 0
1-3-07-1 | 360 | D1 | 8 | 175 |  |  | 0
1-3-07-2 | 360 | D1 | 8 | 175 |  |  | 0
1-3-07-3 | 360 | D1 | 8 | 175 |  |  | 0
1-3-07-4 | 360 | D1 | 8 | 175 |  |  | 0
RTU1-3-07 |  |  |  | 700 |  | 0 | 0
NOTES:

## RTU1 SGRD's (7)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-3-08-1 | 352 | D1 | 8 | 200 |  |  | 0
1-3-08-2 | 352 | D1 | 8 | 200 |  |  | 0
1-3-08-3 | 352 | D1 | 8 | 200 |  |  | 0
1-3-08-4 | 352 | D1 | 8 | 200 |  |  | 0
RTU1-3-08 |  |  |  | 800 |  | 0 | 0
1-4-01-1 | 461 | D2 | 6 | 100 |  |  | 0
1-4-01-2 | 461 | D2 | 6 | 100 |  |  | 0
1-4-01-3 | 461 | D2 | 10 | 300 |  |  | 0
1-4-01-4 | 461 | D2 | 10 | 300 |  |  | 0
RTU1-4-01 |  |  |  | 800 |  | 0 | 0
1-4-02-1 | 405 | LD1 | 4'-0" | 200 |  |  | 0
1-4-02-2 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-3 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-4 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-5 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-6 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-7 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-8 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-9 | 405 | LD1 | 4'-0" | 220 |  |  | 0
1-4-02-10 | 405 | LD1 | 4'-0" | 220 |  |  | 0
RTU1-4-02 |  |  |  | 2180 |  | 0 | 0
1-4-03-1 | 456 | D1 | 8 | 225 |  |  | 0
1-4-03-2 | 456 | D1 | 8 | 225 |  |  | 0
1-4-03-3 | 456 | D1 | 8 | 225 |  |  | 0
RTU1-4-03 |  |  |  | 675 |  | 0 | 0
1-4-04-1 | 454 | D1 | 8 | 150 |  |  | 0
RTU1-4-04 |  |  |  | 150 |  | 0 | 0
1-4-05-1 | 452 | D1 | 6 | 100 |  |  | 0
RTU1-4-05 |  |  |  | 100 |  | 0 | 0
NOTES:

## RTU1 SGRD's (8)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-5-01-1 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-2 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-3 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-4 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-5 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-6 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-7 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-8 | 560 | LD2 | 4'-0" | 165 |  |  | 0
1-5-01-9 | 560 | LD2 | 4'-0" | 165 |  |  | 0
RTU1-5-01 |  |  |  | 1485 |  | 0 | 0
1-5-02-1 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-02-2 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-3 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-4 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-5 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-02-6 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-7 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-8 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-02-9 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-10 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-02-11 | [1] | LD4 | 4'-0" | 250 |  |  | 0
RTU1-5-02 |  |  |  | 3200 |  | 0 | 0
1-5-03-1 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-2 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-3 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-4 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-03-5 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-6 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-7 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-8 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-03-9 | [1] | LD4 | 4'-0" | 250 |  |  | 0
1-5-03-10 | [1] | LD4 | 4'-0" | 250 |  |  | 0
RTU1-5-03 |  |  |  | 2800 |  | 0 | 0
NOTES: | [1] NO ROOM NUMBER ON DRAWING

## RTU1 SGRD's (9)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-5-04-1 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-04-2 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-04-3 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-04-4 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-04-5 | [1] | LD5 | 4'-0" | 400 |  |  | 0
1-5-04-6 | [1] | LD5 | 4'-0" | 400 |  |  | 0
RTU1-5-04 |  |  |  | 2400 |  | 0 | 0
NOTES: | [1] NO ROOM NUMBER ON DRAWING

## RTU-2 VAV's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-2 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU2-1-01 | 109 | REHEAT | SINGLE | 8 | 300 |  | 300
RTU2-2-01 | 207 | REHEAT | SINGLE | 10 | 800 |  | 375
RTU2-2-02 | 206 | REHEAT | SINGLE | 14 | 1425 |  | 850
RTU2-3-01 | 300 | REHEAT | SINGLE | 12 | 1200 |  | 800
RTU2-3-02 | 306 | REHEAT | SINGLE | 10 | 700 |  | 700
RTU2-3-03 | 310 | COOL | SINGLE | 10 | 650 |  | 650
RTU2-3-04 | 305 | REHEAT | SINGLE | 14 | 1710 |  | 1200
RTU2-3-05 | 319 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU2-3-06 | 325 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU2-3-07 | 320 | REHEAT | SINGLE | 16 | 1800 |  | 900
RTU2-3-08 | 324 | REHEAT | SINGLE | 10 | 600 |  | 250
RTU2-3-09 | 320 | REHEAT | SINGLE | 6 | 170 |  | 170
RTU2-4-01 | 402 | REHEAT | SINGLE | 12 | 1200 |  | 700
RTU2-4-02 | 406 | REHEAT | SINGLE | 10 | 950 |  | 950
RTU2-4-03 | 405 | REHEAT | SINGLE | 16 | 2000 |  | 1200
RTU2-4-04 | 417 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU2-4-05 | 419 | REHEAT | SINGLE | 6 | 150 |  | 150
RTU2-4-06 |  | REHEAT | SINGLE
RTU2-4-07 | 416 | REHEAT | SINGLE | 12 | 1200 |  | 750
RTU2-4-08 | 418 | REHEAT | SINGLE | 8 | 400 |  | 250
RTU2-4-09 | 420 | REHEAT | SINGLE | 6 | 300 |  | 200
RTU2-4-10 | 421 | REHEAT | SINGLE | 10 | 800 |  | 580
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU-2 VAV's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-2 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU2-5-01 | 555 | REHEAT | SINGLE | 8 | 600 |  | 400
RTU2-5-02 | 557 | REHEAT | SINGLE | 6 | 100 |  | 80
RTU2-5-03 | 505 | REHEAT | SINGLE | 16 | 2000 |  | 1100
RTU2-5-04 | 553 | REHEAT | SINGLE | 10 | 700 |  | 350
RTU2-5-05 | 551 | REHEAT | SINGLE | 8 | 475 |  | 400
RTU2-5-06 | 506 | REHEAT | SINGLE | 10 | 950 |  | 950
RTU2-5-07 | 505 | REHEAT | SINGLE | 16 | 2500 |  | 1400
RTU2-5-08 | 519 | REHEAT | SINGLE | 12 | 1100 |  | 900
RTU2-5-09 | 517 | REHEAT | SINGLE | 12 | 1000 |  | 800
RTU2-5-10 | 518 | REHEAT | SINGLE | 6 | 175 |  | 150
RTU2-5-11 | 526 | REHEAT | SINGLE | 12 | 1300 |  | 850
RTU2-5-12 | 520 | REHEAT | SINGLE | 12 | 990 |  | 750
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU2 SGRD's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-1-01-1 | 108 | D2 | 8 | 150 |  |  | 0
2-1-01-2 | 109 | D2 | 8 | 150 |  |  | 0
RTU2-1-01 |  |  |  | 300 |  | 0 | 0
2-2-01-1 | 207 | D1 | 8 | 200 |  |  | 0
2-2-01-2 | 207 | D1 | 8 | 200 |  |  | 0
2-2-01-3 | 207 | D1 | 8 | 200 |  |  | 0
2-2-01-4 | 207 | D1 | 8 | 200 |  |  | 0
RTU2-2-01 |  |  |  | 800 |  | 0 | 0
2-2-02-1 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-2 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-3 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-4 | 206 | D1 | 10 | 275 |  |  | 0
2-2-02-5 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-6 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-7 | 206 | D1 | 10 | 275 |  |  | 0
2-2-02-8 | 206 | LD1 | 4'-0" | 125 |  |  | 0
2-2-02-9 | 206 | LD1 | 4'-0" | 125 |  |  | 0
RTU2-2-02 |  |  |  | 1425 |  | 0 | 0
2-3-01-1 | 302 | LD3 | 4'-0" | 300 |  |  | 0
2-3-01-2 | 302 | D4 | 10 | 150 |  |  | 0
2-3-01-3 | 302 | D4 | 10 | 150 |  |  | 0
2-3-01-4 | 302 | LD3 | 4'-0" | 300 |  |  | 0
2-3-01-5 | 302 | D4 | 10 | 150 |  |  | 0
2-3-01-6 | 302 | D4 | 10 | 150 |  |  | 0
RTU2-3-01 |  |  |  | 1200 |  | 0 | 0
2-3-02-1 | 306 | D2 | 12 | 350 |  |  | 0
2-3-02-2 | 308 | D2 | 12 | 350 |  |  | 0
RTU2-3-02 |  |  |  | 700 |  | 0 | 0
2-3-03-1 | 310 | R5 | 14X8 | 650 |  |  | 0
RTU2-3-03 |  |  |  | 650 |  | 0 | 0
NOTES:

## RTU2 SGRD's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-3-04-1 | 305 | LD1 | 4'-0" | 190 |  |  | 0
2-3-04-2 | 305 | LD1 | 4'-0" | 190 |  |  | 0
2-3-04-3 | 305 | LD1 | 4'-0" | 190 |  |  | 0
2-3-04-4 | 305 | LD1 | 4'-0" | 190 |  |  | 0
2-3-04-5 | 305 | LD1 | 4'-0" | 190 |  |  | 0
2-3-04-6 | 305 | LD2 | 4'-0" | 190 |  |  | 0
2-3-04-7 | 305 | LD2 | 4'-0" | 190 |  |  | 0
2-3-04-8 | 305 | LD2 | 4'-0" | 190 |  |  | 0
2-3-04-9 | 305 | LD2 | 4'-0" | 190 |  |  | 0
RTU2-3-04 |  |  |  | 1710 |  | 0 | 0
2-3-05-1 | 319 | D1 | 8 | 200 |  |  | 0
2-3-05-2 | 319 | D1 | 8 | 200 |  |  | 0
2-3-05-3 | 319 | D1 | 8 | 200 |  |  | 0
2-3-05-4 | 319 | D1 | 8 | 200 |  |  | 0
RTU2-3-05 |  |  |  | 800 |  | 0 | 0
2-3-06-1 | 325 | D1 | 8 | 200 |  |  | 0
2-3-06-2 | 325 | D1 | 8 | 200 |  |  | 0
2-3-06-3 | 325 | D1 | 8 | 200 |  |  | 0
2-3-06-4 | 325 | D1 | 8 | 200 |  |  | 0
RTU2-3-06 |  |  |  | 800 |  | 0 | 0
2-3-07-1 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-2 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-3 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-4 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-5 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-6 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-7 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-8 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-9 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-10 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-11 | 320 | D1 | 8 | 150 |  |  | 0
2-3-07-12 | 320 | D1 | 8 | 150 |  |  | 0
RTU2-3-07 |  |  |  | 1800 |  | 0 | 0
NOTES: | [1] NO DIFFUSER TYPE OR CFM ON DRAWING

## RTU2 SGRD's (3)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-3-08-1 | 324 | D4 | 10 | 150 |  |  | 0
2-3-08-2 | 324 | D4 | 10 | 150 |  |  | 0
2-3-08-3 | 324 | D4 | 10 | 150 |  |  | 0
2-3-08-4 | 324 | D4 | 10 | 150 |  |  | 0
RTU2-3-08 |  |  |  | 600 |  | 0 | 0
2-3-09-1 | 320C | DUCT | 8 | 65 |  |  | 0
2-3-09-2 | 320B | DUCT | 8 | 105 |  |  | 0
RTU2-3-09 |  |  |  | 170 |  | 0 | 0
2-4-01-1 | 402 | D4 | 10 | 150 |  |  | 0
2-4-01-2 | 402 | D4 | 10 | 150 |  |  | 0
2-4-01-3 | 402 | LD3 | 4'-0" | 300 |  |  | 0
2-4-01-4 | 402 | D4 | 10 | 150 |  |  | 0
2-4-01-5 | 402 | LD3 | 4'-0" | 300 |  |  | 0
2-4-01-6 | 402 | D4 | 10 | 150 |  |  | 0
RTU2-4-01 |  |  |  | 1200 |  | 0 | 0
2-4-02-1 | 410 | R5 | 12X10 | 250 |  |  | 0
2-4-02-2 | 406 | D2 | 12 | 350 |  |  | 0
2-4-02-3 | 408 | D2 | 12 | 350 |  |  | 0
RTU2-4-02 |  |  |  | 950 |  | 0 | 0
2-4-03-1 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-2 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-3 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-4 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-5 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-6 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-7 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-8 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-9 | 405 | LD1 | 4'-0" | 200 |  |  | 0
2-4-03-10 | 405 | LD1 | 4'-0" | 200 |  |  | 0
RTU2-4-03 |  |  |  | 2000 |  | 0 | 0
2-4-04-1 | 417 | D1 | 8 | 200 |  |  | 0
2-4-04-2 | 417 | D1 | 8 | 200 |  |  | 0
2-4-04-3 | 417 | D1 | 8 | 200 |  |  | 0
2-4-04-4 | 417 | D1 | 8 | 200 |  |  | 0
RTU2-4-04 |  |  |  | 800 |  | 0 | 0
NOTES:

## RTU2 SGRD's (4)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-4-05-1 | 419 | D1 | 8 | 150 |  |  | 0
RTU2-4-05 |  |  |  | 150 |  | 0 | 0
2-4-07-1 | 416 | D1 | 10 | 300 |  |  | 0
2-4-07-2 | 416 | D1 | 10 | 300 |  |  | 0
2-4-07-3 | 416 | D1 | 10 | 300 |  |  | 0
2-4-07-4 | 416 | D1 | 10 | 300 |  |  | 0
RTU2-4-07 |  |  |  | 1200 |  | 0 | 0
2-4-08-1 | 418 | D1 | 8 | 200 |  |  | 0
2-4-08-2 | 418 | D1 | 8 | 200 |  |  | 0
RTU2-4-08 |  |  |  | 400 |  | 0 | 0
2-4-09-1 | 420 | D1 | 10 | 250 |  |  | 0
2-4-09-2 | 422 | D1 | 6 | 50 |  |  | 0
RTU2-4-09 |  |  |  | 300 |  | 0 | 0
2-4-10-1 | 421 | D1 | 8 | 200 |  |  | 0
2-4-10-2 | 421 | D1 | 8 | 200 |  |  | 0
2-4-10-3 | 421 | D1 | 8 | 200 |  |  | 0
2-4-10-4 | 421 | D1 | 8 | 200 |  |  | 0
RTU2-4-10 |  |  |  | 800 |  | 0 | 0
2-5-01-1 | 555 | D1 | 8 | 150 |  |  | 0
2-5-01-2 | 559 | R5 | 12X8 | 125 |  |  | 0
2-5-01-3 | 559 | R5 | 12X8 | 125 |  |  | 0
2-5-01-4 | HALL | LD1 | 4'-0" | 200 |  |  | 0
RTU2-5-01 |  |  |  | 600 |  | 0 | 0
2-5-02-1 | 557 | D1 | 6 | 100 |  |  | 0
RTU2-5-02 |  |  |  | 100 |  | 0 | 0
NOTES:

## RTU2 SGRD's (5)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-5-03-1 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-2 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-3 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-4 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-5 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-6 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-7 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-8 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-9 | 505 | LD1 | 4'-0" | 200 |  |  | 0
2-5-03-10 | 505 | LD1 | 4'-0" | 200 |  |  | 0
RTU2-5-03 |  |  |  | 2000 |  | 0 | 0
2-5-04-1 | 553 | D1 | 8 | 175 |  |  | 0
2-5-04-2 | 553 | D1 | 8 | 175 |  |  | 0
2-5-04-3 | 553 | D1 | 8 | 175 |  |  | 0
2-5-04-4 | 553 | D1 | 8 | 175 |  |  | 0
RTU2-5-04 |  |  |  | 700 |  | 0 | 0
2-5-05-1 | 551 | D1 | 10 | 275 |  |  | 0
2-5-05-1 | 500 | LD2 | 4'-0" | 200 |  |  | 0
RTU2-5-05 |  |  |  | 475 |  | 0 | 0
2-5-06-1 | 510 | R5 | 12X10 | 250 |  |  | 0
2-5-06-2 | 506 | D2 | 12 | 350 |  |  | 0
2-5-06-3 | 508 | D2 | 12 | 350 |  |  | 0
RTU2-5-06 |  |  |  | 950 |  | 0 | 0
2-5-07-1 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-2 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-3 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-4 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-5 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-6 | 505 | LD1 | 4'-0" | 250 |  |  | 0
2-5-07-7 | 505 | LD2 | 4'-0" | 250 |  |  | 0
2-5-07-8 | 505 | LD2 | 4'-0" | 250 |  |  | 0
2-5-07-9 | 505 | LD2 | 4'-0" | 250 |  |  | 0
2-5-07-10 | 505 | LD2 | 4'-0" | 250 |  |  | 0
|  |  |  | 2500 |  | 0 | 0
NOTES:

## RTU2 SGRD's (6)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-5-08-1 | 519 | D1 | 10 | 275 |  |  | 0
2-5-08-2 | 519 | D1 | 10 | 275 |  |  | 0
2-5-08-3 | 519 | D1 | 10 | 275 |  |  | 0
2-5-08-4 | 519 | D1 | 10 | 275 |  |  | 0
RTU2-5-08 |  |  |  | 1100 |  | 0 | 0
2-5-09-1 | 517 | D1 | 10 | 250 |  |  | 0
2-5-09-2 | 517 | D1 | 10 | 250 |  |  | 0
2-5-09-3 | 517 | D1 | 10 | 250 |  |  | 0
2-5-09-4 | 517 | D1 | 10 | 250 |  |  | 0
RTU2-5-09 |  |  |  | 1000 |  | 0 | 0
2-5-10-1 | 518 | D1 | 8 | 175 |  |  | 0
RTU2-5-10 |  |  |  | 175 |  | 0 | 0
2-5-11-1 | 526 | D1 | 6 | 100 |  |  | 0
2-5-11-2 | 526 | D1 | 10 | 300 |  |  | 0
2-5-11-3 | 526 | D1 | 10 | 300 |  |  | 0
2-5-11-4 | 526 | D1 | 10 | 300 |  |  | 0
2-5-11-5 | 526 | D1 | 10 | 300 |  |  | 0
RTU2-5-11 |  |  |  | 1300 |  | 0 | 0
2-5-12-1 | 520 | D4 | 10 | 165 |  |  | 0
2-5-12-2 | 520 | D4 | 10 | 165 |  |  | 0
2-5-12-3 | 520 | D4 | 10 | 165 |  |  | 0
2-5-12-4 | 520 | D4 | 10 | 165 |  |  | 0
2-5-12-5 | 520 | D4 | 10 | 165 |  |  | 0
2-5-12-6 | 520 | D4 | 10 | 165 |  |  | 0
RTU2-5-12 |  |  |  | 990 |  | 0 | 0
NOTES:

## RTU-3 VAV's
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-3 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU3-3-01 | 330 | REHEAT | SINGLE | 8 | 400 |  | 580 |  |  |  |  | MIN > MAX?
RTU3-3-02 | 331 | REHEAT | SINGLE | 6 | 250 |  | 150
RTU3-3-03 | 334 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU3-3-04 | 335 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU3-3-05 | 337 | REHEAT | SINGLE | 6 | 150 |  | 150
RTU3-3-06 | 339 | REHEAT | SINGLE | 12 | 1000 |  | 800
RTU3-3-07 | 305 | REHEAT | SINGLE | 12 | 600 |  | 450
RTU3-3-08 | 338 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU3-3-09 | 336 | REHEAT | SINGLE | 8 | 450 |  | 150
RTU3-4-01 | 423 | REHEAT | SINGLE | 8 | 400 |  | 150
RTU3-4-02 | 426 | REHEAT | SINGLE | 8 | 350 |  | 150
RTU3-4-03 | 428 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU3-4-04 | 430 | REHEAT | SINGLE | 8 | 450 |  | 150
RTU3-4-05 | 429 | REHEAT | SINGLE | 6 | 150 |  | 150
RTU3-4-06 | 431 | REHEAT | SINGLE | 12 | 1100 |  | 900
RTU3-4-07 | 405 | REHEAT | SINGLE | 12 | 600 |  | 450
RTU3-4-08 | 432 | REHEAT | SINGLE | 10 | 800 |  | 580
RTU3-5-01 | 525 | REHEAT | SINGLE | 8 | 400 |  | 150
RTU3-5-02 | 529 | REHEAT | SINGLE | 10 | 1000 |  | 580
RTU3-5-03 | 534 | REHEAT | SINGLE | 12 | 1000 |  | 800
RTU3-5-04 | 531 | REHEAT | SINGLE | 6 | 175 |  | 150
RTU3-5-05 | 533 | REHEAT | SINGLE | 12 | 1200 |  | 900
RTU3-5-06 | 505 | REHEAT | SINGLE | 12 | 600 |  | 450
RTU3-5-07 | 530 | REHEAT | SINGLE | 8 | 475 |  | 200
RTU3-5-08 | 532 | REHEAT | SINGLE | 12 | 1000 |  | 800
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU3 SGRD's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-3-01-1 | 330 | D1 | 8 | 200 |  |  | 0
3-3-01-2 | 330 | D1 | 8 | 200 |  |  | 0
RTU3-3-01 |  |  |  | 400 |  | 0 | 0
3-3-02-1 | 327 | D1 | 6 | 75 |  |  | 0
3-3-02-2 | 331 | D1 | 8 | 225 |  |  | 0
RTU3-3-02 |  |  |  | 300 |  | 0 | 0
3-3-03-1 | 334 | D1 | 8 | 200 |  |  | 0
3-3-03-2 | 334 | D1 | 8 | 200 |  |  | 0
3-3-03-3 | 334 | D1 | 8 | 200 |  |  | 0
3-3-03-4 | 334 | D1 | 8 | 200 |  |  | 0
RTU3-3-03 |  |  |  | 800 |  | 0 | 0
3-3-04-1 | 335 | D1 | 8 | 200 |  |  | 0
3-3-04-2 | 335 | D1 | 8 | 200 |  |  | 0
3-3-04-3 | 335 | D1 | 8 | 200 |  |  | 0
3-3-04-4 | 335 | D1 | 8 | 200 |  |  | 0
RTU3-3-04 |  |  |  | 800 |  | 0 | 0
3-3-05-1 | 337 | D1 | 8 | 150 |  |  | 0
RTU3-3-05 |  |  |  | 150 |  | 0 | 0
3-3-06-1 | 339 | D1 | 10 | 250 |  |  | 0
3-3-06-2 | 339 | D1 | 10 | 250 |  |  | 0
3-3-06-3 | 339 | D1 | 10 | 250 |  |  | 0
3-3-06-4 | 339 | D1 | 10 | 250 |  |  | 0
RTU3-3-06 |  |  |  | 1000 |  | 0 | 0
3-3-07-1 | 305 | LD1 | 6'-0" | 300 |  |  | 0
3-3-07-2 | 305 | LD1 | 6'-0" | 300 |  |  | 0
RTU3-3-07 |  |  |  | 600 |  | 0 | 0
3-3-08-1 | 338 | D1 | 8 | 200 |  |  | 0
3-3-08-2 | 338 | D1 | 8 | 200 |  |  | 0
3-3-08-3 | 338 | D1 | 8 | 200 |  |  | 0
3-3-08-4 | 338 | D1 | 8 | 200 |  |  | 0
RTU3-3-08 |  |  |  | 800 |  | 0 | 0
NOTES:

## RTU3 SGRD's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-3-09-1 | 336 | D1 | 8 | 150 |  |  | 0
3-3-09-2 | 336 | LD1 | 4'-0" | 300 |  |  | 0
RTU3-3-09 |  |  |  | 450 |  | 0 | 0
3-4-01-1 | 423 | D1 | 8 | 150 |  |  | 0
3-4-01-2 | 423 | D1 | 8 | 150 |  |  | 0
3-4-01-3 | 425 | D1 | 6 | 100 |  |  | 0
RTU3-4-01 |  |  |  | 400 |  | 0 | 0
3-4-02-1 | 426 | D4 | 10 | 115 |  |  | 0
3-4-02-2 | 426 | D4 | 10 | 115 |  |  | 0
3-4-02-3 | 426 | D4 | 10 | 115 |  |  | 0
RTU3-4-02 |  |  |  | 345 |  | 0 | 0
3-4-03-1 | 428 | D1 | 8 | 200 |  |  | 0
3-4-03-2 | 428 | D1 | 8 | 200 |  |  | 0
3-4-03-3 | 428 | D1 | 8 | 200 |  |  | 0
3-4-03-4 | 428 | D1 | 8 | 200 |  |  | 0
RTU3-4-03 |  |  |  | 800 |  | 0 | 0
3-4-04-1 | 427 | D1 | 8 | 200 |  |  | 0
3-4-04-2 | 427 | D1 | 8 | 200 |  |  | 0
3-4-04-3 | 427 | D1 | 8 | 200 |  |  | 0
3-4-04-4 | 427 | D1 | 8 | 200 |  |  | 0
RTU3-4-04 |  |  |  | 800 |  | 0 | 0
3-4-05-1 | 429 | D1 | 8 | 150 |  |  | 0
RTU3-4-05 |  |  |  | 150 |  | 0 | 0
3-4-06-1 | 431 | D1 | 10 | 275 |  |  | 0
3-4-06-2 | 431 | D1 | 10 | 275 |  |  | 0
3-4-06-3 | 431 | D1 | 10 | 275 |  |  | 0
3-4-06-4 | 431 | D1 | 10 | 275 |  |  | 0
RTU3-4-06 |  |  |  | 1100 |  | 0 | 0
3-4-07-1 | 405 | LD1 | 6'-0" | 300 |  |  | 0
3-4-07-2 | 405 | LD1 | 6'-0" | 300 |  |  | 0
RTU3-4-07 |  |  |  | 600 |  | 0 | 0
NOTES:

## RTU3 SGRD's (3)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-4-08-1 | 432 | D1 | 8 | 200 |  |  | 0
3-4-08-2 | 432 | D1 | 8 | 200 |  |  | 0
3-4-08-3 | 432 | D1 | 8 | 200 |  |  | 0
3-4-08-4 | 432 | D1 | 8 | 200 |  |  | 0
RTU3-4-08 |  |  |  | 800 |  | 0 | 0
3-4-09-1 | 336 | D1 | 8 | 150 |  |  | 0
3-4-09-2 | 336 | LD1 | 4'-0" | 300 |  |  | 0
RTU3-4-09 |  |  |  | 450 |  | 0 | 0
3-5-01-1 | 525 | D1 | 8 | 150 |  |  | 0
3-5-01-2 | 525 | D1 | 8 | 150 |  |  | 0
3-5-01-3 | 527 | D1 | 6 | 100 |  |  | 0
RTU3-5-01 |  |  |  | 400 |  | 0 | 0
3-5-02-1 | 529 | D1 | 10 | 250 |  |  | 0
3-5-02-2 | 529 | D1 | 10 | 250 |  |  | 0
3-5-02-3 | 529 | D1 | 10 | 250 |  |  | 0
3-5-02-4 | 529 | D1 | 10 | 250 |  |  | 0
RTU3-5-02 |  |  |  | 1000 |  | 0 | 0
3-5-03-1 | 534 | D1 | 10 | 250 |  |  | 0
3-5-03-2 | 534 | D1 | 10 | 250 |  |  | 0
3-5-03-3 | 534 | D1 | 10 | 250 |  |  | 0
3-5-03-4 | 534 | D1 | 10 | 250 |  |  | 0
RTU3-5-03 |  |  |  | 1000 |  | 0 | 0
3-5-04-1 | 531 | D1 | 8 | 175 |  |  | 0
RTU3-5-04 |  |  |  | 175 |  | 0 | 0
3-5-05-1 | 532 | D1 | 10 | 300 |  |  | 0
3-5-05-2 | 532 | D1 | 10 | 300 |  |  | 0
3-5-05-3 | 532 | D1 | 10 | 300 |  |  | 0
3-5-05-4 | 532 | D1 | 10 | 300 |  |  | 0
RTU3-5-05 |  |  |  | 1200 |  | 0 | 0
3-5-06-1 | 505 | LD1 | 6'-0" | 300 |  |  | 0
3-5-06-2 | 505 | LD1 | 6'-0" | 300 |  |  | 0
RTU3-5-06 |  |  |  | 600 |  | 0 | 0
NOTES:

## RTU3 SGRD's (4)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-5-07-1 | 530 | D1 | 8 | 175 |  |  | 0
3-5-07-2 | 530 | LD1 | 4'-0" | 300 |  |  | 0
RTU3-5-07 |  |  |  | 475 |  | 0 | 0
3-5-08-1 | 532 | D1 | 10 | 250 |  |  | 0
3-5-08-2 | 532 | D1 | 10 | 250 |  |  | 0
3-5-08-3 | 532 | D1 | 10 | 250 |  |  | 0
3-5-08-4 | 532 | D1 | 10 | 250 |  |  | 0
RTU3-5-08 |  |  |  | 1000 |  | 0 | 0
NOTES:

## RTU-5 VAV's
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-5 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU5-1-01 | C112 | REHEAT | SINGLE | 10 | 800 |  | 550
RTU5-1-02 | C114 | REHEAT | SINGLE | 8 | 475 |  | 230
RTU5-1-03 | C120 | REHEAT | SINGLE | 8 | 450 |  | 230
RTU5-1-04 | C122 | REHEAT | SINGLE | 10 | 800 |  | 550
RTU5-1-05 | C110 | REHEAT | SINGLE | 10 | 700 |  | 350
RTU5-1-06 | C101 | REHEAT | SINGLE | 12 | 950 |  | 600
RTU5-1-07 | C137 | REHEAT | SINGLE | 8 | 525 |  | 230
RTU5-1-08 | C124 | REHEAT | SINGLE | 6 | 300 |  | 120
RTU5-1-09 | C136 | REHEAT | SINGLE | 8 | 525 |  | 230
RTU5-1-10 | C130 | REHEAT | SINGLE | 8 | 550 |  | 230
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU5 SGRD's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU5 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
5-1-01-1 | C112 | D1 | 10 | 270 |  |  | 0
5-1-01-2 | C112 | D1 | 10 | 260 |  |  | 0
5-1-01-3 | C112 | D1 | 10 | 270 |  |  | 0
RTU5-1-01 |  |  |  | 800 |  | 0 | 0
5-1-02-1 | C114 | D1 | 8 | 250 |  |  | 0
5-1-02-2 | C116 | D1 | 8 | 225 |  |  | 0
RTU5-1-02 |  |  |  | 475 |  | 0 | 0
5-1-03-1 | C118 | D1 | 8 | 225 |  |  | 0
5-1-03-2 | C120 | D1 | 8 | 225 |  |  | 0
RTU5-1-03 |  |  |  | 450 |  | 0 | 0
5-1-04-1 | C122 | D1 | 10 | 270 |  |  | 0
5-1-04-2 | C122 | D1 | 10 | 265 |  |  | 0
5-1-04-3 | C122 | D1 | 10 | 265 |  |  | 0
RTU5-1-04 |  |  |  | 800 |  | 0 | 0
5-1-05-1 | C110 | D1 | 10 | 350 |  |  | 0
5-1-05-2 | C110 | D1 | 10 | 350 |  |  | 0
RTU5-1-05 |  |  |  | 700 |  | 0 | 0
5-1-06-1 | C101 | D1 | 8 | 175 |  |  | 0
5-1-06-2 | C101 | D1 | 8 | 175 |  |  | 0
5-1-06-3 | C101 | D1 | 8 | 175 |  |  | 0
5-1-06-4 | C101 | D1 | 8 | 175 |  |  | 0
5-1-06-5 | C144 | D1 | 10 | 250 |  |  | 0
RTU5-1-06 |  |  |  | 950 |  | 0 | 0
5-1-07-1 | C123 | R5 | 6X6 | 25 |  |  | 0
5-1-07-2 | C123 | D1 | 6 | 100 |  |  | 0
5-1-07-3 | HALL | D1 | 6 | 75 |  |  | 0
5-1-07-4 | C125 | D1 | 6 | 75 |  |  | 0
5-1-07-5 | C119 | D1 | 6 | 100 |  |  | 0
5-1-07-6 | C137 | D1 | 8 | 150 |  |  | 0
RTU5-1-07 |  |  |  | 525 |  | 0 | 0
#DIV/0!
#DIV/0!
#DIV/0!
NOTES:

## RTU5 SGRD's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU5 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
5-1-08-1 | C133 | R5 | 6X6 | 50 |  |  | 0
5-1-08-2 | C124 | D1 | 8 | 200 |  |  | 0
5-1-08-3 | C126 | D1 | 6 | 50 |  |  | 0
RTU5-1-08 |  |  |  | 300 |  | 0 | 0
5-1-09-1 | C136 | D1 | 10 | 250 |  |  | 0
5-1-09-2 | C142 | D1 | 8 | 175 |  |  | 0
5-1-09-3 | C140 | D1 | 6 | 100 |  |  | 0
RTU5-1-09 |  |  |  | 525 |  | 0 | 0
5-1-10-1 | C130 | D1 | 10 | 275 |  |  | 0
5-1-10-2 | C130 | D1 | 10 | 275 |  |  | 0
RTU5-1-10 |  |  |  | 550 |  | 0 | 0
NOTES:

## RTU-6 VAV's
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU-6 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
RTU6-1-01 | 114 | REHEAT | SINGLE | 16 | 1200 |  | 400
RTU6-1-02 | 110 | REHEAT | SINGLE | 6 | 250 |  | 230
RTU6-1-03 | 114.1 | REHEAT | SINGLE | 12 | 1500 |  | 600
RTU6-1-04 | 114 | REHEAT | SINGLE | 16 | 1360 |  | 400
RTU6-1-05 | 116 | REHEAT | SINGLE | 12 | 990 |  | 990
RTU6-1-06 | 125 | REHEAT | SINGLE | 14 | 1820 |  | 1820
RTU6-1-07 | 125 | REHEAT | SINGLE | 14 | 1780 |  | 1620
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU6 SGRD's (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU6 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
6-1-01-1 | 114 | D1 | 10 | 300 |  |  | 0
6-1-01-2 | 114 | D1 | 10 | 300 |  |  | 0
6-1-01-3 | 114 | D1 | 10 | 300 |  |  | 0
6-1-01-4 | 114 | D1 | 10 | 300 |  |  | 0
RTU6-1-01 |  |  |  | 1200 |  | 0 | 0
6-1-02-1 | 110 | R5 | 12X8 | 250 |  |  | 0
RTU6-1-02 |  |  |  | 250 |  | 0 | 0
6-1-03-1 | 114.1 | D1 | 12 | 500 |  |  | 0
6-1-03-2 | 114.1 | D1 | 12 | 500 |  |  | 0
6-1-03-3 | 114.1 | D1 | 12 | 500 |  |  | 0
RTU6-1-03 |  |  |  | 1500 |  | 0 | 0
6-1-04-1 | 114 | D1 | 10 | 300 |  |  | 0
6-1-04-2 | 114 | D1 | 10 | 300 |  |  | 0
6-1-04-3 | 115 | D1 | 8 | 160 |  |  | 0
6-1-04-4 | 114 | D1 | 10 | 300 |  |  | 0
6-1-04-5 | 114 | D1 | 10 | 300 |  |  | 0
RTU6-1-04 |  |  |  | 1360 |  | 0 | 0
6-1-05-1 | 119 | R5 | 10X6 | 200 |  |  | 0
6-1-05-2 | 113 | D1 | 8 | 150 |  |  | 0
6-1-05-3 | 121 | D1 | 8 | 100 |  |  | 0
6-1-05-4 | 116 | D2 | 6 | 25 |  |  | 0
6-1-05-5 | 118 | R5 | 10X6 | 140 |  |  | 0
6-1-05-6 | 117 | D1 | 10 | 325 |  |  | 0
RTU6-1-05 |  |  |  | 940 |  | 0 | 0
6-1-06-1 | 125 | D1 | 12 | 540 |  |  | 0
6-1-06-2 | 125 | D1 | 12 | 540 |  |  | 0
6-1-06-3 | 127 | D1 | 8 | 200 |  |  | 0
6-1-06-4 | 125 | D1 | 12 | 540 |  |  | 0
RTU6-1-06 |  |  |  | 1820 |  | 0 | 0
NOTES:

## RTU6 SGRD's (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: RTU6 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
6-1-07-1 | 125 | D1 | 12 | 540 |  |  | 0
6-1-07-2 | 125 | D1 | 12 | 540 |  |  | 0
6-1-07-3 | 121 | D1 | 8 | 200 |  |  | 0
6-1-07-4 | 126 | D1 | 6 | 100 |  |  | 0
6-1-07-5 | 121 | D1 | 8 | 200 |  |  | 0
6-1-07-6 | 121 | D1 | 8 | 200 |  |  | 0
RTU6-1-07 |  |  |  | 1780 |  | 0 | 0
NOTES:

## EF1
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF1 |  |  | Area: ART/KILN EXHAUST (HIGH ROOF)
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 120C28DOR91VF |  |  | CFM | 1025
Serial Num |  |  |  |  | Fan RPM | 2127
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1.5
Frame
Horsepower |  | 0.75
Motor Rpm |  | 2800
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | 152 | R1 | 22X10 | 150 |  |  | 0
E1-2 | 152 | R1 | 22X10 | 75 |  |  | 0
E1-3 | 150 | R1 | 22X22 | 400 |  |  | 0
E1-4 | 150 | R1 | 22X22 | 400 |  |  | 0
|  |  |  | 1025 |  | 0 | 0
-

## EF2
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF2 |  |  | Area: TOILET EXHAUST (HIGH ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 135R OR80 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UPBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.33 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 300
Voltage (rated) |  | 115 |  |  | Fan RPM | 1570
Amperage (rated) |  | 7.2 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 7.2
Suction ESP
[5 empty] | Total ESP | 1.25
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E2-1 | 354 | R1 | 22X10 | 75 |  |  | 0
E2-2 | 359 | R1 | 22X10 | 75 |  |  | 0
E2-3 | 358 | R1 | 22X10 | 75 |  |  | 0
E2-4 | 210 | R1 | 22X10 | 75 |  |  | 0
|  |  |  | 300 |  | 0 | 0
-

## EF3
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF3 |  |  | Area: TOILET EXHAUST (HIGH ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 300C 10B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE DNBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 3 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 5375
Voltage (rated) |  | 460 |  |  | Fan RPM | 799
Amperage (rated) |  | 4.8 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 4.8
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E3-1 | 508 | R1 | 22X10 | 500 |  |  | 0
E3-2 | 506 | R1 | 22X10 | 500 |  |  | 0
E3-3 | 504 | R1 | 22X10 | 75 |  |  | 0
E3-4 | 408 | R1 | 22X10 | 500 |  |  | 0
E3-5 | 406 | R1 | 22X10 | 500 |  |  | 0
E3-6 | 401 | R1 | 22X10 | 75 |  |  | 0
E3-7 | 308 | R1 | 22X10 | 500 |  |  | 0
E3-8 | 306 | R1 | 22X10 | 500 |  |  | 0
E3-9 | 304 | R1 | 22X10 | 75 |  |  | 0
E3-10 | 203 | R1 | 22X10 | 500 |  |  | 0
E3-11 | 202 | R1 | 22X10 | 500 |  |  | 0
E3-12 | 201 | R1 | 22X10 | 75 |  |  | 0
E3-13 | 109 | R1 | 22X10 | 500 |  |  | 0
E3-14 | 108 | R1 | 22X10 | 500 |  |  | 0
E3-15 | 107 | R1 | 22X10 | 75 |  |  | 0
|  |  |  | 5375 |  | 0 | 0
-

## EF4
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF4 |  |  | Area: COMMUNITY SERVICES EXHAUST (LOW ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 135C OR91 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE DNBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.33 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 450
Voltage (rated) |  | 115 |  |  | Fan RPM | 1360
Amperage (rated) |  | 7.2 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 7.2
Suction ESP
Total ESP
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E4-1 | C128 | R1 | 22X10 | 75 |  |  | 0
E4-2 | C136 | R1 | 22X10 | 75 |  |  | 0
E4-3 | C138 | R1 | 22X10 | 75 |  |  | 0
E4-4 | C102 | R1 | 22X10 | 75 |  |  | 0
E4-5 | C121 | R1 | 22X10 | 150 |  |  | 0
|  |  |  | 450 |  | 0 | 0
-

## EF5
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF5 |  |  | Area: KITCHEN HOOD EXHAUST (LOW ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 300VX11B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UPBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 4400
Voltage (rated) |  | 460 |  |  | Fan RPM | 1165
Amperage (rated) |  | 7.6 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 7.6
Suction ESP
[5 empty] | Total ESP | 2.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E5-1 | 114 | DUCT |  | 2200 |  |  | 0
E5-2 | 114 | DUCT |  | 2200 |  |  | 0
|  |  |  | 4400 |  | 0 | 0
-

## EF6
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF6 |  |  | Area: DISHWASHER HOOD EXHAUST (LOW ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 210RX7B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UPBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 1 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 1200
Voltage (rated) |  | 460 |  |  | Fan RPM | 1192
Amperage (rated) |  | 2.1 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 2.1
Suction ESP
[5 empty] | Total ESP | 1.5
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E6-1 | 114.1 | DUCT |  | 600 |  |  | 0
E6-2 | 114.1 | DUCT |  | 600 |  |  | 0
|  |  |  | 1200 |  | 0 | 0
-

## EF7
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF7 |  |  | Area: GENERAL EXHAUST (ABOVE CEILING)
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | GNVF-180 |  |  | CFM | 150
Serial Num |  |  |  |  | Fan RPM | 0.25
Type |  | INLINE |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 1.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP
Frame
Horsepower
Motor Rpm
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E7-1 | 118 | R2 | 8X6 | 150 |  |  | 0
-

## EF8
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF8 |  |  | Area: TOILET EXHAUST (HIGH ROOF)
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 135C28DOR70VF |  |  | CFM | 450
Serial Num |  |  |  |  | Fan RPM | 2079
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP | 1.5
Motor MFG |  |  |  |  | Total ESP
Frame
Horsepower |  | 0.75
Motor Rpm |  | 2800
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E8-1 | 522 | R1 | 22X10 | 75 |  |  | 0
E8-2 | 424 | R1 | 22X10 | 75 |  |  | 0
E8-3 | 328 | R1 | 22X10 | 75 |  |  | 0
E8-4 | 328 | R1 | 22X10 | 75 |  |  | 0
E8-5 | 323 | R1 | 22X10 | 75 |  |  | 0
E8-6 | 321 | R1 | 22X10 | 75 |  |  | 0
|  |  |  | 450 |  | 0 | 0
-

## EF9
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF9 |  |  | Area: SCIENCE LAB EXHAUST (HIGH ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 135R5B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UPBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 1200
Voltage (rated) |  | 115 |  |  | Fan RPM | 1276
Amperage (rated) |  | 9.8 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 9.8
Suction ESP
[5 empty] | Total ESP | 0.75
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E9-1 | 526 | R1 | 22X22 | 1200 |  |  | 0
-

## EF10
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF10 |  |  | Area: GYM STORAGE EXHAUST (ABOVE CEILING)
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 100SQN17DEC |  |  | CFM | 600
Serial Num |  |  |  |  | Fan RPM | 1370
Type |  | INLINE |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP | 0.25
Motor MFG |  |  |  |  | Total ESP
Frame
Horsepower |  | 0.25
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E10-1 | 139 | R1 | 22X22 | 600 |  |  | 0
-

## EF11
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF11 |  |  | Area: MAIN MECHANICAL 130 (LOW ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 120C4B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE DNBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.33 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 1250
Voltage (rated) |  | 115 |  |  | Fan RPM | 1317
Amperage (rated) |  | 7.2 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 7.2
Suction ESP
[5 empty] | Total ESP | 0.25
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E11-1 | 130 | R2 | 24X14 | 1250 |  |  | 0
-

## EF12
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF12 |  |  | Area: TRASH 134 (ABOVE CEILING)
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 90SQN17DEC |  |  | CFM | 325
Serial Num |  |  |  |  | Fan RPM | 1619
Type |  | INLINE |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.5
Frame
Horsepower |  | 0.167
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E12-1 | 134 | R2 | 12X12 | 325 |  |  | 0
-

## EF13
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: EF13 |  |  | Area: DISHWASHER ROOM EXHAUST (LOW ROOF)
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 150RH5B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UPBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.5 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 800
Voltage (rated) |  | 115 |  |  | Fan RPM | 1415
Amperage (rated) |  | 9.8 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 9.8
Suction ESP
[5 empty] | Total ESP | 1
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E13-1 | 114.1 | R1 | 22X10 | 800 |  |  | 0
-

## Boilers
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: BOILER
Unit Data | B1 |  | B2
Manufacturer | ADVANCED THERMAL HYDRONICS |  | ADVANCED THERMAL HYDRONICS
Model Number | KN20 |  | KN20
Serial Number
Test Data | Design | Actual | Design | Actual | Design | Actual
Water Flow GPM | 120 |  | 120
Water Press. Drop

## HWP1
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: HWP1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | GRUNDFOS | Pump Off Pressure (psi)
Model Num | 25709 VL | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in) | 5.62
Service | HOT WATER | Valve Open GPM
Pump RPM | 1760 | Valve Open Diff (ft)
GPM/Head | 120 / 25.13 | Discharge Pressure (ft)
Impellar Diameter | 5.62 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 25.13
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 145JM | RL Voltage | 480
Horsepower | 1.50 | RL Amperage
Motor RPM | 1800 | BHP
Phase | 3
Voltage | 480
Amperage
Service Factor | 1.15
Efficiency | 67.89
Power Factor

## HWP2
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: HWP2
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | GRUNDFOS | Pump Off Pressure (psi)
Model Num | 25709 VL | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in) | 5.62
Service | HOT WATER | Valve Open GPM
Pump RPM | 1760 | Valve Open Diff (ft)
GPM/Head | 120 / 25.13 | Discharge Pressure (ft)
Impellar Diameter | 5.62 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 25.13
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 145JM | RL Voltage | 480
Horsepower | 1.50 | RL Amperage
Motor RPM | 1800 | BHP
Phase | 3
Voltage | 480
Amperage
Service Factor | 1.15
Efficiency | 67.89
Power Factor

## HWP3
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: HWP3
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | GRUNDFOS | Pump Off Pressure (psi)
Model Num | 25957 LCS | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in) | 8.93
Service | HOT WATER | Valve Open GPM
Pump RPM | 1775 | Valve Open Diff (ft)
GPM/Head | 240 / 74.93 | Discharge Pressure (ft)
Impellar Diameter | 8.93 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 74.93
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 213TC | RL Voltage | 480
Horsepower | 1800 | RL Amperage
Motor RPM | 7.50 | BHP
Phase | 3
Voltage | 480
Amperage
Service Factor | 1.15
Efficiency | 79.15
Power Factor

## HWP4
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: HWP4
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | GRUNDFOS | Pump Off Pressure (psi)
Model Num | 25957 LCS | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in) | 8.93
Service | HOT WATER | Valve Open GPM
Pump RPM | 1775 | Valve Open Diff (ft)
GPM/Head | 240 / 74.93 | Discharge Pressure (ft)
Impellar Diameter | 8.93 | Suction Pressure (ft)
|  | Total Head Pressure (ft) | 74.93
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG | BALDOR | System Set Point
Frame | 213TC | RL Voltage | 480
Horsepower | 1800 | RL Amperage
Motor RPM | 7.50 | BHP
Phase | 3
Voltage | 480
Amperage
Service Factor | 1.15
Efficiency | 79.15
Power Factor

## Circuit Setter (1)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: CIRCUIT SETTERS |  |  |  | Service: HOT WATER | [6 empty] | MY NOTES, DON'T PRINT!
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | CS #
UH-1 | 130 |  |  |  |  | 3.6 |  |  |  |  | CS-1
UH-2 | 130 |  |  |  |  | 3.6 |  |  |  |  | CS-2
UH-3 | 134 |  |  |  |  | 1.9 |  |  |  |  | CS-3
UH-4 | 135 |  |  |  |  | 1.9 |  |  |  |  | CS-4
CUH-1 | 121 |  |  |  |  | 1.9 |  |  |  |  | CS-5
CUH-2 | 127 |  |  |  |  | 1.9 |  |  |  |  | CS-6
RTU6-1-07 | 125 |  |  |  |  | 4.7 |  |  |  |  | CS-7
RTU6-1-06 | 125 |  |  |  |  | 5.2 |  |  |  |  | CS-8
CUH-3 | 125 |  |  |  |  | 1.9 |  |  |  |  | CS-9
RTU6-1-05 | 119 |  |  |  |  | 2.9 |  |  |  |  | CS-10
RTU5-1-10 | C130 |  |  |  |  | 0.7 |  |  |  |  | CS-11
RTU5-1-09 | C136 |  |  |  |  | 0.7 |  |  |  |  | CS-12
RTU5-1-06 | C135 |  |  |  |  | 1.7 |  |  |  |  | CS-13
CUH-4 | C100 |  |  |  |  | 1.9 |  |  |  |  | CS-14
RTU5-1-08 | C124 |  |  |  |  | 0.3 |  |  |  |  | CS-15
RTU5-1-07 | C125 |  |  |  |  | 0.7 |  |  |  |  | CS-16
RTU5-1-04 | C122 |  |  |  |  | 1.6 |  |  |  |  | CS-17
RTU5-1-03 | C118 |  |  |  |  | 0.7 |  |  |  |  | CS-18
RTU5-1-02 | C114 |  |  |  |  | 0.7 |  |  |  |  | CS-19
RTU5-1-05 | C110 |  |  |  |  | 1 |  |  |  |  | CS-20
FT-1 | C110 |  |  |  |  | 0.6 |  |  |  |  | CS-21
FT-2 | C112 |  |  |  |  | 0.7 |  |  |  |  | CS-22
FT-3 | C112 |  |  |  |  | 0.9 |  |  |  |  | CS-23
RTU5-1-01 | C112 |  |  |  |  | 1.6 |  |  |  |  | CS-24
RTU6-1-04 | 114 |  |  |  |  | 1.2 |  |  |  |  | CS-25
RTU6-1-03 | 114 |  |  |  |  | 1.7 |  |  |  |  | CS-26
RTU6-1-01 | 114 |  |  |  |  | 1.2 |  |  |  |  | CS-27
RTU6-1-02 | 114 |  |  |  |  | 0.7 |  |  |  |  | CS-28
RTU2-1-01 | 109 |  |  |  |  | 0.9 |  |  |  |  | CS-29
CUH-5 | 106 |  |  |  |  | 1.9 |  |  |  |  | CS-30
RTU1-1-09 | 102 |  |  |  |  | 2.4 |  |  |  |  | CS-31
CUH-6 | 100 |  |  |  |  | 2.3 |  |  |  |  | CS-32
RTU1-1-08 | 100 |  |  |  |  | 1.3 |  |  |  |  | CS-33
RTU1-1-07 | 154 |  |  |  |  | 0.9 |  |  |  |  | CS-34
RTU1-1-10 | 150 |  |  |  |  | 0.6 |  |  |  |  | CS-35
RTU1-1-10 [1] | 150 |  |  |  |  | 4 |  |  |  |  | CS-36
FT-4 | 145.1 |  |  |  |  | 1.4 |  |  |  |  | CS-37
CS-38
NOTES: | [1] DUPLICATE TAG

## Circuit Setter (2)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: CIRCUIT SETTERS |  |  |  | Service: HOT WATER | [6 empty] | MY NOTES, DON'T PRINT!
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | CS #
FT-5 | 142 |  |  |  |  | 1.4 |  |  |  |  | CS-38
FT-6 | 142 |  |  |  |  | 1.4 |  |  |  |  | CS-39
FT-7 | 142 |  |  |  |  | 1.4 |  |  |  |  | CS-40
FT-8 | 142 |  |  |  |  | 0.7 |  |  |  |  | CS-41
FT-9 | 142 |  |  |  |  | 0.6 |  |  |  |  | CS-42
RTU1-2-10 | 202 |  |  |  |  | 2.1 |  |  |  |  | CS-43
RTU1-2-11 | 200 |  |  |  |  | 3.5 |  |  |  |  | CS-44
RTU2-2-01 | 207 |  |  |  |  | 1.1 |  |  |  |  | CS-45
RTU2-2-02 | 206 |  |  |  |  | 2.4 |  |  |  |  | CS-46
RTU1-2-09 | 200 |  |  |  |  | 2.3 |  |  |  |  | CS-47
RTU1-2-08 | 200 |  |  |  |  | 3.5 |  |  |  |  | CS-48
RTU-1-2-06 | 200 |  |  |  |  | 4 |  |  |  |  | CS-49
RTU1-2-07 | 200 |  |  |  |  | 1.3 |  |  |  |  | CS-50
RTU1-2-01 | 212 |  |  |  |  | 3.6 |  |  |  |  | CS-51
RTU1-2-02 | 212 |  |  |  |  | 2 |  |  |  |  | CS-52
RTU1-2-05 | 200 |  |  |  |  | 1.7 |  |  |  |  | CS-53
RTU1-2-04 | 200 |  |  |  |  | 3.5 |  |  |  |  | CS-54
RTU1-2-03 | 200 |  |  |  |  | 3.5 |  |  |  |  | CS-55
RTU2-3-09 | 320 |  |  |  |  | 0.6 |  |  |  |  | CS-56
RTU2-3-05 | 319 |  |  |  |  | 1.7 |  |  |  |  | CS-57
RTU2-3-06 | 325 |  |  |  |  | 1.7 |  |  |  |  | CS-58
RTU2-3-07 | 324 |  |  |  |  | 2.6 |  |  |  |  | CS-59
RTU2-3-08 | 330 |  |  |  |  | 0.7 |  |  |  |  | CS-60
RTU3-3-02 | 335 |  |  |  |  | 0.6 |  |  |  |  | CS-61
RTU3-3-01 | 334 |  |  |  |  | 1.7 |  |  |  |  | CS-62
RTU3-3-03 | 334 |  |  |  |  | 1.7 |  |  |  |  | CS-63
RTU3-3-05 | 335 |  |  |  |  | 0.6 |  |  |  |  | CS-64
RTU3-3-04 | 335 |  |  |  |  | 1.7 |  |  |  |  | CS-65
RTU3-3-07 | 339 |  |  |  |  | 1.3 |  |  |  |  | CS-66
RTU3-3-06 | 339 |  |  |  |  | 2.3 |  |  |  |  | CS-67
RTU-3-3-09 | 336 |  |  |  |  | 0.6 |  |  |  |  | CS-68
RTU3-3-08 | 338 |  |  |  |  | 1.7 |  |  |  |  | CS-69
RTU2-3-04 | 319 |  |  |  |  | 3.5 |  |  |  |  | CS-70
RTU2-3-02 | 305 |  |  |  |  | 1.5 |  |  |  |  | CS-71
RTU-2-3-01 | 300 |  |  |  |  | 2.3 |  |  |  |  | CS-72
RTU1-3-08 | 354 |  |  |  |  | 1.7 |  |  |  |  | CS-73
RTU1-3-07 | 360 |  |  |  |  | 1.7 |  |  |  |  | CS-74
NOTES:

## Circuit Setter (3)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: CIRCUIT SETTERS |  |  |  | Service: HOT WATER | [6 empty] | MY NOTES, DON'T PRINT!
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | CS #
RTU1-3-06 | 357 |  |  |  |  | 1.7 |  |  |  |  | CS-75
RTU1-3-05 | 356 |  |  |  |  | 1.7 |  |  |  |  | CS-76
RTU1-3-04 | 361 |  |  |  |  | 3.2 |  |  |  |  | CS-77
RTU1-3-03 | 362 |  |  |  |  | 0.6 |  |  |  |  | CS-78
RTU1-3-02 | 364 |  |  |  |  | 0.6 |  |  |  |  | CS-79
RTU1-3-01 | 361 |  |  |  |  | 1 |  |  |  |  | CS-80
RTU2-4-02 | 405 |  |  |  |  | 2.1 |  |  |  |  | CS-81
RTU2-4-01 | 402 |  |  |  |  | 2 |  |  |  |  | CS-82
RTU1-4-03 | 456 |  |  |  |  | 1.2 |  |  |  |  | CS-83
RTU1-4-05 | 452 |  |  |  |  | 0.6 |  |  |  |  | CS-84
RTU1-4-04 | 456 |  |  |  |  | 0.6 |  |  |  |  | CS-85
RTU1-4-02 | 405 |  |  |  |  | 3.5 |  |  |  |  | CS-86
RTU1-4-01 | 405 |  |  |  |  | 1.3 |  |  |  |  | CS-87
RTU2-4-03 | 417 |  |  |  |  | 3.5 |  |  |  |  | CS-88
RTU2-4-04 | 417 |  |  |  |  | 1.7 |  |  |  |  | CS-89
RTU2-4-05 | 417 |  |  |  |  | 0.6 |  |  |  |  | CS-90
RTU2-4-07 | 416 |  |  |  |  | 2.2 |  |  |  |  | CS-91
RTU2-4-08 | 418 |  |  |  |  | 0.7 |  |  |  |  | CS-92
RTU2-4-09 | 418 |  |  |  |  | 0.6 |  |  |  |  | CS-93
RTU2-4-10 | 421 |  |  |  |  | 1.7 |  |  |  |  | CS-94
RTU3-4-01 | 423 |  |  |  |  | 0.6 |  |  |  |  | CS-95
RTU3-4-04 | 427 |  |  |  |  | 1.7 |  |  |  |  | CS-96
RTU3-4-02 | 428 |  |  |  |  | 0.6 |  |  |  |  | CS-97
RTU3-4-03 | 428 |  |  |  |  | 1.7 |  |  |  |  | CS-98
RTU3-4-05 | 427 |  |  |  |  | 0.6 |  |  |  |  | CS-99
RTU3-4-06 | 431 |  |  |  |  | 2.6 |  |  |  |  | CS-100
RTU3-4-07 | 431 |  |  |  |  | 1.3 |  |  |  |  | CS-101
RTU3-4-09 | 430 |  |  |  |  | 0.6 |  |  |  |  | CS-102
RTU3-4-08 | 432 |  |  |  |  | 1.7 |  |  |  |  | CS-103
FT-10 | 461 |  |  |  |  | 1.2 |  |  |  |  | CS-104
FT-11 | 461 |  |  |  |  | 1.2 |  |  |  |  | CS-105
FT-12 | 461 |  |  |  |  | 1.2 |  |  |  |  | CS-106
FT-13 | 461 |  |  |  |  | 1.2 |  |  |  |  | CS-107
RTU2-5-08 | 519 |  |  |  |  | 2.6 |  |  |  |  | CS-108
RTU2-5-11 | 526 |  |  |  |  | 2.4 |  |  |  |  | CS-109
RTU2-5-10 | 518 |  |  |  |  | 0.6 |  |  |  |  | CS-110
RTU2-5-09 | 517 |  |  |  |  | 2.3 |  |  |  |  | CS-111
NOTES:

## Circuit Setter (4)
National TAB
Project: Greater Dayton School BP2
Address: Deeds Park Dr. Dayton, OH
Asset: CIRCUIT SETTERS |  |  |  | Service: HOT WATER | [6 empty] | MY NOTES, DON'T PRINT!
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | CS #
RTU2-5-12 | 520 |  |  |  |  | 2.2 |  |  |  |  | CS-112
RTU3-5-01 | 525 |  |  |  |  | 0.6 |  |  |  |  | CS-113
RTU3-5-02 | 529 |  |  |  |  | 1.7 |  |  |  |  | CS-114
RTU3-5-03 | 534 |  |  |  |  | 2.3 |  |  |  |  | CS-115
RTU3-5-04 | 529 |  |  |  |  | 0.6 |  |  |  |  | CS-116
RTU3-5-07 | 532 |  |  |  |  | 0.6 |  |  |  |  | CS-117
RTU3-5-06 | 533 |  |  |  |  | 1.3 |  |  |  |  | CS-118
RTU3-5-05 | 533 |  |  |  |  | 2.6 |  |  |  |  | CS-119
RTU3-5-08 | 532 |  |  |  |  | 2.3 |  |  |  |  | CS-120
RTU2-5-07 | 505 |  |  |  |  | 4 |  |  |  |  | CS-121
RTU2-5-06 | 505 |  |  |  |  | 2.1 |  |  |  |  | CS-122
RTU2-5-05 | 553 |  |  |  |  | 0.6 |  |  |  |  | CS-123
RTU2-5-04 | 553 |  |  |  |  | 0.6 |  |  |  |  | CS-124
RTU2-5-03 | 553 |  |  |  |  | 3.2 |  |  |  |  | CS-125
RTU2-5-02 | 553 |  |  |  |  | 0.6 |  |  |  |  | CS-126
RTU2-5-01 | 553 |  |  |  |  | 0.6 |  |  |  |  | CS-127
RTU1-5-04 | 560 |  |  |  |  | 2.3 |  |  |  |  | CS-128
RTU1-5-03 | 560 |  |  |  |  | 4.6 |  |  |  |  | CS-129
RTU1-5-02 | 560 |  |  |  |  | 5.2 |  |  |  |  | CS-130
RTU1-5-01 | 560 |  |  |  |  | 2.4 |  |  |  |  | CS-131
NOTES: