## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9815 | 7400 | 7716 | 2100 | 2099 | 22.11% | 21.39%
AC-2 | DINING A | 2510 | 2628 | 1960 | 2114 | 550 | 514 | 21.91% | 19.56%
AC-3 | DINING B | 5000 | 5234 | 3925 | 4111 | 1075 | 1123 | 21.5% | 21.46%
AC-4 | PLAY AREA | 1800 | 1903 | 1500 | 1575 | 300 | 328 | 16.67% | 17.24%
AC-5 | BOH | 1200 | 1277 | 1020 | 1093 | 180 | 184 | 15% | 14.41%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1982
EF-2 | HOOD 2 | [10 empty] | 701 | 707
EF-3 | RESTROOM | [12 empty] | 500 | 513
EF-4 | HOOD 3 | [10 empty] | 390 | 397
TOTALS |  | 20010 | 20857 | 15805 | 16609 | 4205 | 4248 |  |  | 0 | 0 | 3003 | 3086 | 500 | 513
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4205 | 4248 |  | FRONT |  | 0.0027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3503 | 3599 |  | SIDE |  | 0.0019 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 702 | 649 |  | REAR |  | 0.0047 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0031 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Economizers on AC#2 & 3 do not work.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390