## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8085 | 6500 | 6228 | 2000 | 1857 | 23.53% | 22.97%
AC-2 | SIDE DINING | 3150 | 3046 | 2400 | 2282 | 750 | 764 | 23.81% | 25.08%
AC-3 | MAIN DINING | 4000 | 4007 | 3000 | 2993 | 1000 | 1014 | 25% | 25.31%
AC-4 | MAIN DINING | 2765 | 2683 | 2165 | 2042 | 600 | 641 | 21.7% | 23.89%
AC-5 | PLAY AREA | 2000 | 1844 | 1700 | 1523 | 300 | 321 | 15% | 17.41%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1923
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1424
EF-3 | RESTROOM | [12 empty] | 500 | 447
TOTALS |  | 20415 | 19665 | 15765 | 15068 | 4650 | 4597 |  |  | 0 | 0 | 3314 | 3347 | 500 | 447
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4597 |  | FRONT |  | 0.03 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3794 |  | SIDE |  | 0.03 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 836 | 803 |  | REAR |  | 0.03 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.03 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390