## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9800 | 10001 | 8320 | 8619 | 1480 | 1382 | 15.1% | 13.82%
AC-2 | SERVING/ DRIVE THRU | 5250 | 4792 | 3975 | 3638 | 1275 | 1154 | 24.29% | 24.08%
AC-3 | DINING | 6000 | 5903 | 3975 | 3991 | 2025 | 1912 | 33.75% | 32.39%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1952
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1267
EF-3 | RESTROOM | [12 empty] | 400 | 416
TOTALS |  | 21050 | 20696 | 16270 | 16248 | 4780 | 4448 |  |  | 0 | 0 | 3314 | 3219 | 400 | 416
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4780 | 4448 |  | FRONT |  | 0.0086 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3635 |  | SIDE |  | 0.0101 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1066 | 813 |  | REAR |  | 0.0061 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0082667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390