## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING ROOM | 5000 | 4296 | 4110 | 3408 | 890 | 888 | 17.8% | 20.67%
DOAS-1 | KITCHEN | 2300 | 2313 | 0 | 0 | 2300 | 2313 | 100% | 100%
KEF-1 | GRIDDLE HOOD | [10 empty] | 1600 | 1604
KEF-2 | FRYER HOOD | [10 empty] | 775 | 773
EF-1 | WOMENS RR | [12 empty] | 75 | 94
EF-2 | MENS RR | [12 empty] | 75 | 99
TOTALS |  | 7300 | 6609 | 4110 | 3408 | 3190 | 3201 |  |  | 0 | 0 | 2375 | 2377 | 150 | 193
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3190 | 3201 |  | FRONT |  | 0.0051 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2525 | 2570 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 665 | 631 |  | REAR |  | 0.0047 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0049 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0