## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FRONT SALES | 2625 | 2841 | 2187 | 2437 | 438 | 404 | 16.69% | 14.22%
RTU-2 | FRONT SALES | 2275 | 2431 | 2175 | 2323 | 100 | 108 | 4.396% | 4.443%
RTU-3 | REAR SALES | 1750 | 1880 | 1650 | 1782 | 100 | 98 | 5.714% | 5.213%
RTU-4 | REAR SALES | 1400 | 1507 | 1300 | 1413 | 100 | 94 | 7.143% | 6.238%
RTU-5 | PHARMACY | 2275 | 2435 | 2175 | 2334 | 100 | 101 | 4.396% | 4.148%
RTU-6 | STOCKROOM | 1400 | 1489 | 1300 | 1380 | 100 | 109 | 7.143% | 7.32%
RTU-7 | FRONT SALES | 1750 | 1868 | 1650 | 1759 | 100 | 109 | 5.714% | 5.835%
EF-1 | OFFICE | [12 empty] | 300 | 0
EF-2 | BREAK ROOM | [12 empty] | 300 | 274
EF-3 | RESTROOM | [12 empty] | 250 | 243
EF-4 | RESTROOM | [12 empty] | 405 | 368
EF-5 | PHOTO | [12 empty] | 0 | 0
TOTALS |  | 13475 | 14451 | 12437 | 13428 | 1038 | 1023 |  |  | 0 | 0 | 0 | 0 | 1255 | 885
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1038 | 1023 |  | FRONT |  | 0.0089 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1255 | 885 |  | SIDE |  | 0.0049 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -217 | 138 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0069 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Rear door sets off alarm did not take measurement. Office exhaust fan not functional, is beign replaced once up and running should bring net airflow into the negative.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0