## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 3600 | 3733 | 2900 | 3048 | 700 | 685 | 19.44% | 18.35%
RTU-2 | SALES | 3250 | 3284 | 2870 | 2893 | 380 | 391 | 11.69% | 11.91%
RTU-3 | FOH | 2000 | 1989 | 1800 | 1785 | 200 | 204 | 10% | 19.66%
EF-1 | RESTROOMS | [12 empty] | 375 | 378
EF-2 | BOH | [12 empty] | 400 | 430
EF-3 | TRASH | [12 empty] | 200 | 185
TOTALS |  | 8850 | 9006 | 7570 | 7726 | 1280 | 1280 |  |  | 0 | 0 | 0 | 0 | 975 | 993
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1280 | 1280 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 975 | 993 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 305 | 287 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0