## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 3150 | 3387 | 2850 | 3099 | 300 | 288 | 9.524% | 8.503%
RTU-2 |  | 2100 | 2197 | 1725 | 1835 | 375 | 362 | 17.86% | 16.48%
RTU-3 |  | 3570 | 3737 | 2940 | 3074 | 630 | 663 | 17.65% | 17.74%
RTU-4 |  | 2000 | 2074 | 2000 | 2074 | 0 | 0 | 0% | 0%
RTU-5 |  | 1260 | 1266 | 1081 | 1068 | 179 | 198 | 14.21% | 15.64%
RTU-6 |  | 1260 | 1300 | 1215 | 1222 | 45 | 78 | 3.571% | 6%
EF-1 | [13 empty] | 550 | 576
EF-2 | [13 empty] | 450 | 458
TOTALS |  | 13340 | 13961 | 11811 | 12372 | 1529 | 1589 |  |  | 0 | 0 | 0 | 0 | 1000 | 1034
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1529 | 1589 |  | FRONT |  | 0.0082 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1000 | 1034 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 529 | 555 |  | REAR |  | 0.0031 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00565 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0