## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3500 | 3750 | 2300 | 2512 | 1200 | 1238 | 34.29% | 33.01%
RTU-2 | KITCHEN | 2000 | 1862 | 1400 | 1290 | 600 | 572 | 30% | 30.72%
MUA-1 | HOOD 1 | [8 empty] | 1400 | 1508
EF-1 | HOOD 1 | [10 empty] | 2500 | 2664
EF-2 | HOOD 2 | [10 empty] | 700 | 748
EF-3 | RESTROOMS | [12 empty] | 300 | 277
TOTALS |  | 5500 | 5612 | 3700 | 3802 | 1800 | 1810 |  |  | 1400 | 1508 | 3200 | 3412 | 300 | 277
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3200 | 3318 |  | FRONT |  | -0.0012 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3500 | 3689 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -300 | -371 |  | REAR |  | -0.0006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0