## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BAR & BAR DINING | 4400 | 4464 | 3350 | 3424 | 1050 | 1040 | 23.86% | 23.3%
RTU-2 | WAITING & DINING | 4400 | 4611 | 3350 | 3621 | 1050 | 990 | 23.86% | 21.47%
RTU-3 | KITCHEN | 4400 | 4546 | 3375 | 3590 | 1025 | 956 | 23.3% | 21.03%
MUA-1 | HOOD MUA1 | [8 empty] | 4880 | 4553
EF-1 | HOOD I | [10 empty] | 2205 | 2228
EF-2 | HOOD 2 | [10 empty] | 2125 | 2134
EF-3 | HOOD 3 | [10 empty] | 1480 | 1477
EF-4 | HOOD 4 | [10 empty] | 1050 | 1003
EF-5 | RESTROOMS | [12 empty] | 450 | 433
TOTALS |  | 13200 | 13621 | 10075 | 10635 | 3125 | 2986 |  |  | 4880 | 4553 | 6860 | 6842 | 450 | 433
[16 empty] | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 8005 | 7539 |  | FRONT |  | 0.004
TOTAL EXHAUST |  | 7310 | 7275 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | TRUE
NET AIRFLOW |  | 695 | 264 |  | REAR |  | 0.006
[5 empty] | AVERAGE |  | 0.0043333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
MAU duct leaking above ceiling.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0