## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4500 | 4716 | 3200 | 3336 | 1300 | 1380 | 28.89% | 29.26%
RTU-2 | KITCHEN | 4800 | 5043 | 4550 | 4788 | 250 | 255 | 5.208% | 5.057%
FCU-1 | OFFICE |  |  |  |  | 40 | 42 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 2250 | 2078
KEF-1 | HOOD 1 | [10 empty] | 875 | 922
KEF-2 | HOOD 2 | [10 empty] | 1886 | 1751
EF-1 | RESTROOMS | [10 empty] | 480 | 481
TOTALS |  | 9300 | 9759 | 7750 | 8124 | 1590 | 1677 |  |  | 2250 | 2078 | 3241 | 3154 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3840 | 3755 |  | FRONT |  | 0.0176 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3241 | 3154 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 599 | 601 |  | REAR |  | 0.0172 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0174 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2540 | 2375
TOTAL KITCHEN EXHAUST |  | 2761 | 2673
NET AIRFLOW |  | -221 | -298
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0