## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
OAP-1 | DINING | 1150 | 1194 | 0 | 0 | 1150 | 1194 | 100% | 100%
FCU-5 | OFFICE |  |  |  |  | 40 | 41
FCU-6 | KITCHEN | 1700 | 1627 | 1700 | 1627 | 0 | 0 | 0% | 0%
FCU-7 | KITCHEN | 1700 | 1665 | 1700 | 1665 | 0 | 0 | 0% | 0%
FCU-8 | KITCHEN | 1700 | 1619 | 1700 | 1619 | 0 | 0 | 0% | 0%
MUA-1 | COOKLINE | [8 empty] | 2000 | 1993
ESP-1 | HOODS | [10 empty] | 2491 | 2484
EF-1 | RESTROOMS | [12 empty] | 225 | 233
TOTALS |  | 6250 | 6105 | 5100 | 4911 | 1190 | 1235 |  |  | 2000 | 1993 | 2491 | 2484 | 225 | 233
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3190 | 3228 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2716 | 2717 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 474 | 511 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0035 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2040 | 2034
TOTAL KITCHEN EXHAUST |  | 2491 | 2484
NET AIRFLOW |  | -451 | -450
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0