## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | MAIN SALES | 5750 | 5741 | 5100 | 5063 | 650 | 678 | 11.3% | 11.81%
RTU-2 | MAIN SALES | 5750 | 5465 | 5100 | 4780 | 650 | 685 | 11.3% | 12.53%
RTU-3 | SALES / OFFICE | 1050 | 1108 | 930 | 984 | 120 | 124 | 11.43% | 11.19%
RTU-4 | SALES / OFFICE | 1800 | 1828 | 1600 | 1618 | 200 | 210 | 11.11% | 11.49%
RTU-5 | SALES / OFFICE | 1200 | 1264 | 1040 | 1095 | 160 | 169 | 13.33% | 13.37%
RTU-6 | IT ROOM | 975 | 1002 | 975 | 1002 | 0 | 0 | 0% | 0%
RTU-7 | SALES / OFFICE | 1500 | 1559 | 1200 | 1252 | 300 | 307 | 20% | 19.69%
RTU-8 | SALES / OFFICE | 1100 | 1145 | 940 | 990 | 160 | 155 | 14.55% | 13.54%
RTU-9 | SERVICE GARAGE | 5600 | 5591 | 1600 | 1569 | 4000 | 4022 | 71.43% | 71.94%
RTU-10 | SERVICE GARAGE | 5600 | 5606 | 1600 | 1533 | 4000 | 4073 | 71.43% | 72.65%
EF-12 | SERVICE GARAGE | [10 empty] | 1500 | 2037
TOTALS |  | 30325 | 30309 | 20085 | 19886 | 10240 | 10423 |  |  | 0 | 0 | 1500 | 2037 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 10240 | 10423 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 1500 | 2037 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 8740 | 8386 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0