## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9898 | 8320 | 8678 | 1180 | 1220 | 12.42% | 12.33%
AC-2 | SERVING | 5250 | 5223 | 3975 | 4055 | 1275 | 1168 | 24.29% | 22.36%
AC-3 | DINING | 6000 | 6091 | 3975 | 4138 | 2025 | 1953 | 33.75% | 32.06%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1694
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1291
EF-3 | RESTROOM | [12 empty] | 300 | 325
TOTALS |  | 20750 | 21212 | 16270 | 16871 | 4480 | 4341 |  |  | 0 | 0 | 3314 | 2985 | 300 | 325
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4480 | 4341 |  | FRONT |  | 0.0248 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3310 |  | SIDE |  | 0.0295 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 866 | 1031 |  | REAR |  | 0.0267 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.027 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390