## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 |  | 2400 | 0 | 600 |  | 20% | #DIV/0!
RTU-2 | WEST KITCHEN | 3000 |  | 2400 | 0 | 600 |  | 20% | #DIV/0!
RTU-3 | SOUTH KITCHEN | 2550 | 2538 | 2040 | 1994 | 510 | 544 | 20% | 21.43%
MUA-1 | HOOD | [8 empty] | 1900 | 1912
KEF-1 | GRIDDLE | [10 empty] | 1600 | 1571
KEF-2 | FRYER | [10 empty] | 775 | 777
KEF-3 | DISHES | [10 empty] | 525 | 544
EF-1 | RR | [12 empty] | 170 | 177
EF-2 | RR | [12 empty] | 170 | 164
TOTALS |  | 8550 | 2538 | 6840 | 1994 | 1710 | 544 |  |  | 1900 | 1912 | 2900 | 2892 | 340 | 341
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3610 | 2456 |  | FRONT |  | 0.0074 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3240 | 3233 |  | SIDE |  | -0.0021 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 370 | -777 |  | REAR |  | 0.0077 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0043333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0