## Report Sheet
STORE #: | 2720 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | BEAVERCREEK, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-17 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | TYLER YOUELLS, DYLAN CHRISMAN | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
TRANE | YHC072F3RMA0RTP | 161710117L | RTU-1 | KITCHEN | 500 | 620 | 0 | 0 |  | 1743 | 1743 | 772 | 772 | 1 | 208.3 | 208.3 | 3 | 4 | 2.63 | 2.61 | 0.91577 | 0.90881 | -0.7605%
TRANE | YHC092F3RHA0HH | 161510032L | RTU-2 | DINING | 1000 | 689 | 1000 | 1031 |  | 1.821V | 1.821V | 1.821V | 1.821V | 3.8 | 209.5 | 209.5 | 3 | 8.5 | 2.55 | 2.57 | 0.89303 | 0.90003 | 0.7843%
CAPTIVE AIRE | A1-D.250-G10 | 2522844 | MUA-1 | HOOD 1 | 1775 | 1193 | 1500 | 1449 | No | 1771 | 1759 | 1221 | 1334 | 2.9 | 209.6 | 209.6 | 3 | 5.9 | 2.95 | 3.11 | 1.0336 | 1.0897 | 5.424%
CAPTIVE AIRE | NCA24HPFA | 2522844 | EF-1 | HOOD 1 | 2925 | 2959 | 2200 | 2202 | Yes | 1722 | 1768 | 1069 | 881 | 2 | 207.8 | 207.8 | 3 | 5.9 | 5.65 | 3.51 | 1.9626 | 1.2193 | -37.88%
| RR FAN RUNNING? | No | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 2502 | 2500 | 2480 |  | FRONT DOOR |  | 0.0022 |  |  | INITIAL | 4.805 | 2502
|  |  | TOTAL EXHAUST |  | 3075 | 2959 | 2350 | 2202 |  | BACK DOOR |  | 0.0019 |  |  | FINAL | 4.1178 | 2480
|  |  | NET AIRFLOW |  | 200 | -457 | 150 | 278 |  | AVERAGE |  | 0.00205 |  |  | ∆ | 0.68726 | 22
Issue List
Unit # | Description
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA | MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU-1/2 | RTU / Intake Filter / The air intake filter is clogged and had to be removed for balancing. Recommend cleaning

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.