## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8638 | 8120 | 7385 | 1380 | 1253 | 14.53% | 14.51%
AC-2 | SERVING/DRIVE THRU | 5600 | 5155 | 4325 | 3853 | 1275 | 1302 | 22.77% | 25.26%
AC-3 | DINING | 6400 | 6004 | 4375 | 4096 | 2025 | 1908 | 31.64% | 31.78%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1855
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1322
EF-3 | RESTROOM | [12 empty] | 300 | 307
TOTALS |  | 21500 | 19797 | 16820 | 15334 | 4680 | 4463 |  |  | 0 | 0 | 3314 | 3177 | 300 | 307
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4680 | 4463 |  | FRONT |  | 0.0175 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3484 |  | SIDE |  | 0.0182 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1066 | 979 |  | REAR |  | 0.018 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0179 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390