## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | BOH | 1475 | 1335 | 1355 | 1221 | 120 | 114 | 8.136% | 8.539%
FCU-2 | STOCKROOM | 1050 | 1083 | 815 | 865 | 235 | 218 | 22.38% | 20.13%
FCU-3 | SALES | 1840 | 1954 | 1520 | 1631 | 320 | 323 | 17.39% | 16.53%
FCU-4 | SALES | 1840 | 1753 | 1520 | 1412 | 320 | 341 | 17.39% | 19.45%
FCU-5 | SOLAR ZONE | 1400 | 1435 | 1080 | 1106 | 320 | 329 | 22.86% | 22.93%
EF-1 | RESTROOMS | [12 empty] | 200 | 207
TOTALS |  | 7605 | 7560 | 6290 | 6235 | 1315 | 1325 |  |  | 0 | 0 | 0 | 0 | 200 | 207
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1315 | 1325 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 200 | 207 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1115 | 1118 |  | REAR |  | 0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0035 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0