## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 7943 | 7000 | 6057 | 1750 | 1886 | 20% | 23.74%
AC-2 | DRIVE THRU | 5250 | 5413 | 4000 | 4216 | 1250 | 1197 | 23.81% | 22.11%
AC-3 | DINNING | 5250 | 5473 | 4100 | 4261 | 1150 | 1212 | 21.9% | 22.15%
AC-4 | BOH | 1875 | 1978 | 1375 | 1437 | 500 | 541 | 26.67% | 27.35%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1992
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1451
EF-3 | RESTROOM | [12 empty] | 375 | 359
TOTALS |  | 21125 | 20807 | 16475 | 15971 | 4650 | 4836 |  |  | 0 | 0 | 3315 | 3443 | 375 | 359
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4836 |  | FRONT |  | 0.0106 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3802 |  | SIDE |  | 0.0148 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 960 | 1034 |  | REAR |  | 0.0134 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0134 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building pressure measurements taken during test mode on all RTUs. Once released from test mode RTUs modulated airflow and outside air damper positions. Technician took multiple pressure readings during modulation and did not observe negative pressures. A building pressure as low as 0.0012" was observed, however.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390