## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 5000 | 4009 | 4145 | 4009 | 855 | 0 | 17.1% | 0%
RTU-2 | DINING | 4000 | 3259 | 3194 | 3259 | 806 | 0 | 20.15% | 0%
MUA-1 | COOKLINE | [8 empty] | 1980 | 2018
KEF-1 | HOOD 1 | [10 empty] | 1600 | 1563
KEF-2 | HOOD 2 | [10 empty] | 775 | 880
KEF-3 | HOOD 3 | [10 empty] | 525 | 521
EF-1 | RESTROOM | [12 empty] | 75 | 69
EF-2 | RESTROOM | [12 empty] | 75 | 72
TOTALS |  | 9000 | 7268 | 7339 | 7268 | 1661 | 0 |  |  | 1980 | 2018 | 2900 | 2964 | 150 | 141
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3641 | 2018 |  | FRONT |  | 0.002 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3050 | 3105 |  | SIDE |  | 0.001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 591 | -1087 |  | REAR |  | 0.061 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.021333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0