## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 794 | 350 | 337
RTU-2 | SALES | 800 | 878 | 350 | 358
RTU-3 | BOH/KITCHEN | 800 | 836 | 350 | 365
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 219 | 225 | 219
EF-2 | MEN'S RR |  |  |  |  | 525 | 537 | 525 | 537
EF-3 | HOOD |  |  |  |  | 1350 | 1335 | 0 | 0
TOTALS |  | 2400 | 2508 | 1050 | 1060 | 2100 | 2091 | 750 | 756
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2508 |  |  | FRONT |  | 0.002 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2091 |  |  | SIDE |  | 0.0033
NET AIRFLOW |  | 300 | 417 |  |  | REAR |  | 0.0012 |  | TRUE
[6 empty] | AVERAGE |  | 0.0021667
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 1060 |  |  | FRONT |  | 0.0023
TOTAL EXHAUST |  | 750 | 756 |  |  | SIDE |  | 0.0029
NET AIRFLOW |  | 300 | 304 |  |  | REAR |  | 0.0017
[6 empty] | AVERAGE |  | 0.0023
NOTES: