## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2000 | 1927 | 1700 | 1619 | 300 | 308 | 15% | 15.98%
RTU-2 | SERVING | 3500 | 3395 | 2800 | 2651 | 700 | 744 | 20% | 21.9%
RTU-3 | DINING | 4000 | 4239 | 3200 | 3374 | 800 | 865 | 20% | 20.41%
EF-1 | MOP SINK | [12 empty] | 75 | 46
PRV-1 | RESTROOMS | [12 empty] | 300 | 0
PRV-4 | RESTROOMS | [12 empty] | 100 | 82
MAU | COOKLINE | [8 empty] | 1800 | 1799
PRV2 | GRIDDLE HD-1 | [10 empty] | 1500 | 1506
PRV3 | FRYER HD-2 | [10 empty] | 1500 | 1622
TOTALS |  | 9500 | 9561 | 7700 | 7644 | 1800 | 1917 |  |  | 1800 | 1799 | 3000 | 3128 | 475 | 128
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  |  | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3600 | 3716 |  | FRONT |  | 0.008" | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3475 | 3256 |  | SIDE |  | 0.008" |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 125 | 460 |  | REAR |  | 0.006" | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0073 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Once PRV-1 is operational, building net airflow should still be near +160cfm.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0