## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2100 | 2168 | 1500 | 1829 | 600 | 339 | 28.57% | 15.64%
RTU-2 | BOH | 2100 | 2334 | 1820 | 2046 | 280 | 288 | 13.33% | 12.34%
RTU-3 | KITCHEN | 2500 | 2419 | 2050 | 1940 | 450 | 479 | 18% | 19.8%
MUA-1 | COOKLINE | [8 empty] | 2764 | 2882
KEF-1 | HD1 | [10 empty] | 1633 | 1712
KEF-2 | HD2 | [10 empty] | 1617 | 1685
EF-1 | RESTROOMS | [12 empty] | 270 | 187
TOTALS |  | 6700 | 6921 | 5370 | 5815 | 1330 | 1106 |  |  | 2764 | 2882 | 3250 | 3397 | 270 | 140
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4094 | 3988 |  | FRONT |  | -0.0034 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 3520 | 3537 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 574 | 451 |  | REAR |  | -0.0044 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0039 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3214 | 3361
TOTAL KITCHEN EXHAUST |  | 3250 | 3397
NET AIRFLOW |  | -36 | -36
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0