## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE | YORK ZJ078 | N1H6928227 | RTU-1 | KITCHEN | 265 | 0 | 0 | 0 | 1758 | 864 | 2 | 215 | 3 | 6.6 | 5.33 | 5.33 | 1.6152 | 1.6152 | 0%
TRANE | YORK ZJ102 | N1H6928187 | RTU-2 | DINING | 700 | 947 | 1000 | 947 | 1760 | 869 | 3 | 216 | 3 | 9.5 | 6.3 | 6.3 | 1.9895 | 1.9895 | 0%
CAPTIVE-AIRE | A1-D.250-G10 | 2654155 | MUA-1 | HOOD 1 | 2085 | 1767 | 1500 | 1517 | 1769/1782 | 1148/960 | 2 | 216% | 3 | 5.95 | 3.06 | 2.83 | 1.0286 | 0.95126 | -7.516%
CAPTIVE-AIRE | NCA16FA | 2654155 | EF-1 | HOOD 1 | 2700 | 2274 | 2200 | 2274 | 1773 | 1075 | 1.5 | 216 | 3 | 5.5 | 3.6 | 3.6 | 0.98182 | 0.98182 | 0%
NL - NOT TESTED | DR12HFA | 2654155 | EF-2 | RESTROOM | 150 | 152 | 150 | 152 | DD | DD | 0.18 | 120 | 1 | 1.9 | 1 | 1 | 0.094737 | 0.094737 | 0%
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3050 | 2714 | 2500 | 2464 | 0.002" | FRONT DOOR | 4.615 | 2714 | INITIAL
|  |  | TOTAL EXHAUST |  | 2850 | 2426 | 2350 | 2426 | 0.0017" | BACK DOOR | 4.5377 | 2464 | FINAL
|  |  | NET AIRFLOW |  | 200 | 288 | 150 | 38 | 0.0018" | AVERAGE | -1.675% | 250 | NET CHANGE

## 2EP-3200
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1950 |  | 1875 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 3200 | 0 | 2650 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3450 | 0 | 2875 | 0 |  | FRONT DOOR | #DIV/0! | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3350 | 150 | 2800 | 150 |  | BACK DOOR | #DIV/0! | 0 | FINAL
|  |  | NET AIRFLOW |  | 100 | -150 | 75 | -150 |  | AVERAGE | #DIV/0! | 0 | NET CHANGE