## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING/RR | 3400 | 3297 | 2400 | 2292 | 1000 | 1005 | 29.41% | 30.48%
RTU-2 | KITCHEN | 5000 | 4921 | 3250 | 3082 | 1750 | 1839 | 35% | 37.37%
EF-1 | GRILL | [10 empty] | 1188 | 1290
EF-2 | FRYER | [10 empty] | 860 | 940
EF-3 | RESTROOMS | [12 empty] | 200 | 206
TOTALS |  | 8400 | 8218 | 5650 | 5374 | 2750 | 2844 |  |  | 0 | 0 | 2048 | 2230 | 200 | 206
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2750 | 2844 |  | FRONT |  | 0.001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2248 | 2436 |  | SIDE |  | 0.001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 502 | 408 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.001 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 0 | 1839
TOTAL KITCHEN EXHAUST |  | 0 | 2230
NET AIRFLOW |  | 0 | -391
BP neutral, could not increase OA for RTU1 due to low flow, OA already increased for RTU2, exhausts for hood set to clear smoke sufficiently.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0