## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6107 | 4400 | 4236 | 1750 | 1871 | 28.46% | 30.64%
RTU-2 | KITCHEN | 6225 | 6033 | 4525 | 4210 | 1700 | 1823 | 27.31% | 30.22%
PRV 2 | HOOD2 | [10 empty] | 1500 | 1594
PRV 3 | HOOD1 | [10 empty] | 1500 | 1594
PRV 1 | RESTROOM | [12 empty] | 300 | 301
EF1A | RESTROOM | [12 empty] | 75 | 82
EF1 | MOP ROOM | [12 empty] | 75 | 80
TOTALS |  | 12375 | 12140 | 8925 | 8446 | 3450 | 3694 |  |  | 0 | 0 | 3000 | 3188 | 450 | 463
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3694 |  | FRONT |  | 0.021 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3651 |  | SIDE |  | 0.016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 43 |  | REAR |  | 0.018 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.018333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0