## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3650 | 3507 | 1533 | 1395 | 2117 | 2112 | 58% | 60.22%
RTU-2 | DINING | 2240 | 2189 | 493 | 444 | 1747 | 1745 | 77.99% | 79.72%
KEF-1 | KITCHEN HD | [10 empty] | 1994 | 1949
KEF-2 | KITCHEN HD | [10 empty] | 1216 | 1126
EF-1 | RESTROOMS | [12 empty] | 300 | 138
TOTALS |  | 5890 | 5696 | 2026 | 1839 | 3864 | 3857 |  |  | 0 | 0 | 3210 | 3075 | 300 | 138
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3864 | 3857 |  | FRONT |  | 0.0381 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3510 | 3213 |  | SIDE |  | 0.0151 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 354 | 644 |  | REAR |  | 0.0127 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.021967
NOTES:
See issues list about EF-1.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0