## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 |  | 2045 | 2569 | 1890 | 2421 | 155 | 148 | 7.579% | 5.761%
FCU-2 |  | 2045 | 2397 | 1890 | 2240 | 155 | 157 | 7.579% | 6.55%
FCU-3 | [5 empty] | 40 | 39 | - | -
OAP-1 |  | 1410 | 1378 | 0 | 0 | 1410 | 1378 | 100% | 100%
OAP-2 |  | 1410 | 1420 | 0 | 0 | 1410 | 1420 | 100% | 100%
KEF-1 | [11 empty] | 2600 | 2621
EF-1 | [13 empty] | 150 | 151
TOTALS |  | 6910 | 7764 | 3780 | 4661 | 3170 | 3142 |  |  | 0 | 0 | 2600 | 2621 | 150 | 151
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3170 | 3142 |  | FRONT |  | 0.0188 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2750 | 2772 |  | SIDE |  | 0.0155 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 420 | 370 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01715 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2820 | 2798
TOTAL KITCHEN EXHAUST |  | 2600 | 2621
NET AIRFLOW |  | 220 | 177
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0