## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | KITCHEN | 2950 | 2953 | 2950 | 2953 | 0 | 0 | 0% | 0%
AHU-2 | DINING | 2950 | 2867 | 2350 | 2357 | 600 | 510 | 20.34% | 17.79%
AHU-3 | DINING | 1300 | 1242 | 1100 | 1072 | 200 | 170 | 15.38% | 13.69%
MUA-1 | KITCHEN HOOD | [8 empty] | 1900 | 1956
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2566
EF-2 | RESTROOM | [12 empty] | 150 | 152
TOTALS |  | 7200 | 7062 | 6400 | 6382 | 800 | 680 |  |  | 1900 | 1956 | 2550 | 2566 | 150 | 152
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2700 | 2636 |  | FRONT |  | -0.007 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2700 | 2718 |  | SIDE |  | -0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -82 |  | REAR |  | -0.007 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0066667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
PRESSURE WITH ALL EQUIPMENT OFF IS -0.003. NET PRESSURE IS -0.004. OA VALUES WERE ESTIMATED BASED ON PRESSURES DUE TO BEING INACCESSIBLE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X16 |  | 2650 |  | 3200 |  | -550