## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 4000 | 3885 | 3200 | 3059 | 800 | 826 | 20% | 21.26%
RTU-2 |  | 2000 | 1640 | 1600 | 1265 | 400 | 375 | 20% | 22.87%
MUA-1 | [10 empty] | 2104
KEF-1 | [12 empty] | 4005
EF-2 | [14 empty] | 0
TOTALS |  | 6000 | 5525 | 4800 | 4324 | 1200 | 1201 |  |  | 0 | 2104 | 0 | 4005 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1200 | 3305 |  | FRONT |  | -0.0022 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 4005 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1200 | -700 |  | REAR |  | -0.0044 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0033 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
EF-2 was found to be not in operation.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0