## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 5500 | 5820 | 4650 | 4960 | 850 | 860 | 15.45% | 14.78%
RTU-2 |  | 5500 | 5917 | 4650 | 5038 | 850 | 879 | 15.45% | 14.86%
RTU-3 |  | 900 | 1062 | 780 | 931 | 120 | 131 | 13.33% | 12.34%
RTU-4 |  | 1100 | 1325 | 900 | 1116 | 200 | 209 | 18.18% | 15.77%
RTU-5 |  | 1700 | 1763 | 1400 | 1473 | 300 | 290 | 17.65% | 16.45%
RTU-6 |  | 1200 | 1317 | 1050 | 1157 | 150 | 160 | 12.5% | 12.15%
RTU-7 |  | 1300 | 1342 | 1100 | 1129 | 200 | 213 | 15.38% | 15.87%
RTU-8 |  | 7000 | 7409 | 2400 | 2534 | 4600 | 4875 | 65.71% | 65.8%
RTU-9 |  | 7000 | 7295 | 2400 | 2776 | 4600 | 4519 | 65.71% | 61.95%
RTU-10 |  | 975 | 985 | 375 | 985 | 600 | 0 | 61.54% | 0%
TOTALS |  | 32175 | 34235 | 19705 | 22099 | 12470 | 12136 |  |  | 0 | 0 | 0 | 0 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 12470 | 12136 |  | FRONT |  | - | [8 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 0 | 0 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 12470 | 12136 |  | REAR |  | - | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0