## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8707 | 6500 | 6688 | 2000 | 2019 | 23.53% | 23.19%
AC-2 | SERVING/ DRIVE THRU | 4000 | 4109 | 3000 | 3072 | 1000 | 1037 | 25% | 25.24%
AC-3 | DINING | 4240 | 4488 | 3040 | 3202 | 1200 | 1286 | 28.3% | 28.65%
AC-4 | PLAY AREA | 1800 | 1721 | 1500 | 1430 | 300 | 291 | 16.67% | 16.91%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1960
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1474
EF-3 | RESTROOM | [12 empty] | 525 | 533
TOTALS |  | 18540 | 19025 | 14040 | 14392 | 4500 | 4633 |  |  | 0 | 0 | 3314 | 3434 | 525 | 533
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4500 | 4633 |  | FRONT |  | 0.0124 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3839 | 3967 |  | SIDE |  | 0.0108 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 661 | 666 |  | REAR |  | 0.0101 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0111 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390