## Report Sheet
STORE #: | 1547 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | Sandusky, Ohio | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 131" LONG HOOD, 9" PSP, FRYER LEFT END PANEL | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-22 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | Dylan Crisman | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | YHC072E3RMA0M3Q | 103912538L | RTU-1 | KITCHEN | 500 | 632 | 0 | 0 |  | 1674 | 1674 | 932 | 932 | 1 | 209.6 | 209.6 | 3 | 4 | 4.26 | 4.13 | 1.4926 | 1.447 | -3.052%
YORK | YHC092E3RHA0M3Q | 104010715L | RTU-2 | DINING | 1000 | 0 | 600 | 712 |  | 1126 | 1126 | 1126 | 1126 | NL | 209.3 | 209.3 | 3 | 8.5 | 6.46 | 6.46 | 2.2602 | 2.2602 | 0%
CAPTIVE AIRE | D76 | 1217059 | MUA-1 | HOOD 1 | 1425 | 1235 | 1000 | 1235 | No | 2152 | 2152 | 1758 | 2152 | 1.5 | 208.9 | 208.9 | 3 | 4.7 | 3.6 | 3.6 | 1.2571 | 1.2571 | 0%
CAPTIVE AIRE | DU85HFA | 2853405 | EF-1 | HOOD 1 | 2150 | 1959 | 1700 | 1747 | No | 1215 | 1143 | 1215 | 1143 | 0.75 | 119.4 | 118.5 | 1 | 7.2 | 8 | 6.1 | 1.5967 | 1.2083 | -24.32%
| RR FAN RUNNING? | No | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 2925 | 1867 | 1600 | 1947 |  | FRONT DOOR |  | 0.0051 |  |  | INITIAL | 6.6067 | 1867
|  |  | TOTAL EXHAUST |  | 2300 | 1959 | 1850 | 1747 |  | BACK DOOR |  | 0.0047 |  |  | FINAL | 6.1727 | 1947
|  |  | NET AIRFLOW |  | 625 | -92 | -250 | 200 |  | AVERAGE |  | 0.0049 |  |  | ∆ | -0.43395 | 80
Issue List
Unit # | Description
MUA-1 | MUA-1 motor pulley is seized and unable to break free. Airflow could not be adjusted.
RTU-2 | RTU / OA Damper / Outside air damper is not functional. OA damper was manually set but could not be left in place. Recommend it be permanently set about 1.25" open.
Additional Notes: | There is an EF-3 that serves a small Type II hood that the manager states is never turned on. It was originally scheduled for 400 CFM. Building pressure set so that the building will only be slightly negative when and if this hood is turned on.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.